## MASTER SPREADSHEET
| Asset Description | Room/Area | Asset Type | Asset Class | Defualt Service Life (YRS) | Year of Installation | Current Asset Age (YRS) | % Service Life Remaining | Utilization Level | Utilization Adjustment | Maintenance/Renewal Level | Renewal Adjustment | Condition Rating | Condition Adjustment | Expected Service Life (YRS) | Expected Remaining Life (YRS) | Replacement Value ($) | Weighting Factor | Weighted Remaining Life (YRS) | Total Weighting Factor | Total Weighted Remaining Life (YRS) | Structural Integrity Rating
EQUIPMENT
WATER TREATMENT PLANT
- | Piping | Pump Room | WAUL | PI | 50 | 2005 | 18 | 64% | Run time is within expected range | 0% | Easily maintained | 10% | Minor Defects Only | 0% | 55 | 37 | 750000 | 0.033309 | 1.2324 | 0.029427 | 1.0888
- | Piping | Pipe Gallery | WAUL | PI | 50 | 2005 | 18 | 64% | Run time is within expected range | 0% | Easily maintained | 10% | Minor Defects Only | 0% | 55 | 37 | 750000 | 0.033309 | 1.2324 | 0.029427 | 1.0888
Generator unit | Generator No. 2 | Exterior | WAUL | GN | 35 | 2004 | 19 | 45.71% | Run time less than expected | 10% | Largely preventative maintenance | 0% | Minor Defects Only | 15% | 43.75 | 24.75 | 750000 | 0.033309 | 0.8244 | 0.029427 | 0.72833
Generator unit | Generator No. 1 | Exterior | WAUL | GN | 35 | 2005 | 18 | 48.57% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 47.25 | 29.25 | 750000 | 0.033309 | 0.97429 | 0.029427 | 0.86075
FE-350B | Flow Element - Finished Water | Finished Water Vault | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Moderate to Significant Deterioration | 15% | 20.25 | 2.25 | 67500 | 0.0029978 | 0.0067451 | 0.0026485 | 0.005959
FE-350B | Flowmeter - Finished Water No. 2 | Finished Water Vault | WAUL | IC | 15 | 2022 | 1 | 93.33% | Run time is within expected range | 0% | Easily maintained | 0% | Moderate to Significant Deterioration | -25% | 11.25 | 10.25 | 67500 | 0.0029978 | 0.030727 | 0.0026485 | 0.027147
FFE-350A | Flowmeter - Finished Water No. 1 | Finished Water Vault | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Virtually Unserviceable | 0% | 18 | 0 | 67500 | 0.0029978 | 0 | 0.0026485 | 0
FE-702 | Flowmeter - Storage Water Tank | Finished Water Vault | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 67500 | 0.0029978 | 0.011242 | 0.0026485 | 0.0099317
FV-703 | Valve - Finished Water No. 703 | Finished Water Vault | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 45000 | 0.0019985 | 0.031477 | 0.0017656 | 0.027809
FV-704 | Valve - Pressure Relief No. 701 | Finished Water Vault | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
FV-704 | Valve - Pressure Relief No. 702 | Finished Water Vault | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
- | Piping | Mechanical Corridor | WAUL | PI | 50 | 2004 | 19 | 62% | Run time is within expected range | 0% | Easily maintained | 10% | Moderate Deterioration | -15% | 47.5 | 28.5 | 150000 | 0.0066618 | 0.18986 | 0.0058855 | 0.16774
BFV-210 | Valve - Raw Water No. 210 Static Mixer No. 210 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
BFV-211 | Valve - Raw Water No. 211 Static Mixer No. 210 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
BFV-BLWR-282-D | Valve - Blower No. 282 Discharge | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 7500 | 0.00033309 | 0.0060789 | 0.00029427 | 0.0053705
BFV-BLWR-282-S | Valve - Blower No. 282 Suction | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 7500 | 0.00033309 | 0.0060789 | 0.00029427 | 0.0053705
BFV-BLWR-281-D | Valve - Blower No. 281 Discharge | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 7500 | 0.00033309 | 0.0060789 | 0.00029427 | 0.0053705
BFV-BLWR-281-S | Valve - Blower No. 281 Suction | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 7500 | 0.00033309 | 0.0060789 | 0.00029427 | 0.0053705
FV-271 | Valve - Finished Water No. 271 UV Reactor No. 270 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
FV-272 | Valve - Finished Water No. 272 UV Reactor No. 270 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
FV-281 | Valve - Finished Water No. 281 UV Reactor No. 280 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
FV-282 | Valve - Finished Water No. 282 UV Reactor No. 280 | Mechanical Corridor | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
WTP-SCADA | SCADA Panel - Treatment Plant Control | Mechanical Corridor | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 22.5 | 120000 | 0.0053294 | 0.11991 | 0.0047084 | 0.10594
FCP-SCDA | SCADA Panel - Filter System Control | Mechanical Corridor | WAUL | IC | 15 | 2004 | 19 | 0% | Run time significantly less than expected | 15% | Easily maintained | 20% | Very Good Condition | 25% | 24 | 5 | 120000 | 0.0053294 | 0.026647 | 0.0047084 | 0.023542
BFV-310 | Valve - Finished Water Pump No. 310 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 37500 | 0.0016654 | 0.030394 | 0.0014714 | 0.026852
BFV-320 | Valve - Finished Water Pump No. 320 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 37500 | 0.0016654 | 0.030394 | 0.0014714 | 0.026852
BFV-330 | Valve - Finished Water Pump No. 330 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 37500 | 0.0016654 | 0.030394 | 0.0014714 | 0.026852
BFV-340 | Valve - Finished Water Pump No. 340 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 37500 | 0.0016654 | 0.030394 | 0.0014714 | 0.026852
FCV-293 | Valve - Backwash Water No. 293 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
FCV-294 | Valve - Backwash Water No. 294 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
BFV-291 | Valve - Backwash Water Pump No. 291 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 22500 | 0.00099927 | 0.018237 | 0.00088282 | 0.016111
BFV-292 | Valve - Backwash Water Pump No. 292 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 22500 | 0.00099927 | 0.018237 | 0.00088282 | 0.016111
CV-291 | Valve - Backwash Water Pump No. 291 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
CV-292 | Valve - Backwash Water Pump No. 292 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
CV-310 | Valve - Finished Water Pump No. 310 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
CV-320 | Valve - Finished Water Pump No. 320 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
CV-330 | Valve - Finished Water Pump No. 330 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
FIT-350B | Transmitter - Finished Water Flowmeter | Pump Room | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 7500 | 0.00033309 | 0.0012491 | 0.00029427 | 0.0011035
FE-295 | Transmitter - Backwash Water Flowmeter FE-295 | Pump Room | WAUL | IC | 15 | 2020 | 3 | 80% | Run time is within expected range | 0% | Easily maintained | 0% | Very Good Condition | 0% | 15 | 12 | 7500 | 0.00033309 | 0.0039971 | 0.00029427 | 0.0035313
FIT-702 | Transmitter - Storage Water Tank Flowmeter | Pump Room | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 7500 | 0.00033309 | 0.0012491 | 0.00029427 | 0.0011035
FIT-295 | Transmitter - Backwash Water Flowmeter FIT-295 | Pump Room | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 7500 | 0.00033309 | 0.0012491 | 0.00029427 | 0.0011035
M-BWP-291 | Motor - Backwash Water Pump No. 291 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 75000 | 0.0033309 | 0.03664 | 0.0029427 | 0.03237
M-BWP--292 | Motor - Backwash Water Pump No. 292 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 75000 | 0.0033309 | 0.03664 | 0.0029427 | 0.03237
M-HSP-310 | Motor - Finished Water Pump No. 310 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 150000 | 0.0066618 | 0.07328 | 0.0058855 | 0.06474
M-HSP-320 | Motor - Finished Water Pump No. 320 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 150000 | 0.0066618 | 0.07328 | 0.0058855 | 0.06474
M-HSP-330 | Motor - Finished Water Pump No. 330 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 150000 | 0.0066618 | 0.07328 | 0.0058855 | 0.06474
M-HSP-340 | Motor - Finished Water Pump No. 340 | Pump Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 150000 | 0.0066618 | 0.07328 | 0.0058855 | 0.06474
P-HSP-330 | Pump - Finished Water No. 330 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 375000 | 0.016654 | 0.32476 | 0.014714 | 0.28692
P-HSP-340 | Pump - Finished Water No. 340 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 375000 | 0.016654 | 0.32476 | 0.014714 | 0.28692
P-HSP-310 | Pump - Finished Water No. 310 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 375000 | 0.016654 | 0.32476 | 0.014714 | 0.28692
P-HSP-320 | Pump - Finished Water No. 320 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 375000 | 0.016654 | 0.32476 | 0.014714 | 0.28692
P-BWW-292 | Pump - Backwash Water No. 292 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 150000 | 0.0066618 | 0.1299 | 0.0058855 | 0.11477
P-BWW-291 | Pump - Backwash Water No. 291 | Pump Room | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 150000 | 0.0066618 | 0.1299 | 0.0058855 | 0.11477
CV-340 | Valve - Finished Water Pump No. 340 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
SLV-330 | Valve - Finished Water Surge Relief No. 330 | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 45000 | 0.0019985 | 0.036473 | 0.0017656 | 0.032223
FV-520 | Valve - EQ Pump No. 520 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 22500 | 0.00099927 | 0.018237 | 0.00088282 | 0.016111
FV-521 | Valve - EQ Pumps No. 521 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FV-522 | Valve - EQ Pumps No. 522 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 22500 | 0.00099927 | 0.018237 | 0.00088282 | 0.016111
FWCV-217A | Valve - Wastewater Flow Control No. 217A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-210 | Valve - Raw Water Flow Control No. 210 Clarifier No. 210 | Pipe Gallery | WAUL | VA | 25 | 2009 | 14 | 44% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 0% | 30 | 16 | 30000 | 0.0013324 | 0.021318 | 0.0011771 | 0.018834
FCV-212 | Valve - Clarifier Effluent No. 212 Clarifier No. 210 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-213A | Valve - Clarified Water No. 213A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-213B | Valve - Clarified Water No. 213B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-215A | Valve - Filtered Water Flow Control No. 215A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-215B | Valve - Filtered Water Flow Control No. 215B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-220 | Valve - Raw Water Flow Control No. 220 Clarifier No. 220 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
FCV-222 | Valve - Clarifier Effluent No. 222 Clarifier No. 220 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-223A | Valve - Clarified Water No. 223A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-223B | Valve - Clarified Water No. 223B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-225A | Valve - Filtered Water Flow Control No. 225A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-225B | Valve - Filtered Water Flow Control No. 225B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-230 | Valve - Raw Water Flow Control No. 230 Clarifier No. 230 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
FCV-232 | Valve - Clarifier Effluent No. 232 Clarifier No. 230 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-233A | Valve - Clarified Water No. 233A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-233B | Valve - Clarified Water No. 233B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-235A | Valve - Filtered Water Flow Control No. 235A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-235B | Valve - Filtered Water Flow Control No. 235B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-240 | Valve - Raw Water Flow Control No. 240 Clarifier No. 240 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
FCV-242 | Valve - Clarifier Effluent No. 242 Clarifier No. 240 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-243A | Valve - Clarified Water No. 243A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-243B | Valve - Clarified Water No. 243B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
FCV-245A | Valve - Filtered Water Flow Control No. 245A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FCV-245B | Valve - Filtered Water Flow Control No. 245B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
BWCV-216A | Valve - Backwash Inlet No. 216A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-216B | Valve - Backwash Inlet No. 216B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-217B | Valve - Wastewater Flow Control No. 217B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
BWCV-219A | Valve - Backwash Outlet No. 219A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-219B | Valve - Backwash Outlet No. 219B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-226A | Valve - Backwash Inlet No. 226A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-226B | Valve - Backwash Inlet No. 226B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-229A | Valve - Backwash Outlet No. 229A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-229B | Valve - Backwash Outlet No. 229B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-236A | Valve - Backwash Inlet No. 236A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-236B | Valve - Backwash Inlet No. 236B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-239A | Valve - Backwash Outlet No. 239A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-239B | Valve - Backwash Outlet No. 239B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-246A | Valve - Backwash Inlet No. 246A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-246B | Valve - Backwash Inlet No. 246B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-249A | Valve - Backwash Outlet No. 249A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
BWCV-249B | Valve - Backwash Outlet No. 249B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.0013324 | 0.020985 | 0.0011771 | 0.018539
ACV-211 | Valve - Air Scour No. 211 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-214A | Valve - Scour Air No. 214A Filter No. 210A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-221 | Valve - Air Scour No. 221 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-224A | Valve - Scour Air No. 224A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-231 | Valve - Air Scour No. 231 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-234A | Valve - Scour Air No. 234A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-241 | Valve - Air Scour No. 241 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
ACV-244A | Valve - Scour Air No. 244A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
BCV-214B | Valve - Scour Air No. 214B Filter No. 210B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
BCV-224B | Valve - Scour Air No. 224B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
BCV-234B | Valve - Scour Air No. 234B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
BCV-244B | Valve - Scour Air No. 244B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 15000 | 0.00066618 | 0.010492 | 0.00058855 | 0.0092696
CWCV-218 | Valve - Clarifier Waste No. 218 Clarifier No. 210 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Moderate Deterioration | 0% | 30 | 12 | 37500 | 0.0016654 | 0.019985 | 0.0014714 | 0.017656
CWCV-228 | Valve - Clarifier Waste No. 228 Clarifier No. 220 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 37500 | 0.0016654 | 0.026231 | 0.0014714 | 0.023174
CWCV-238 | Valve - Clarifier Waste No. 238 Clarifier No. 230 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 37500 | 0.0016654 | 0.026231 | 0.0014714 | 0.023174
CWCV-248 | Valve - Clarifier Waste No. 248 Clarifier No. 240 | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 37500 | 0.0016654 | 0.026231 | 0.0014714 | 0.023174
BPV-550 | Valve - EQ Pumps Backpressure Control | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 22500 | 0.00099927 | 0.018237 | 0.00088282 | 0.016111
FWCV-227A | Valve - Wastewater Flow Control No. 227A Filter No. 220A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FWCV-227B | Valve - Wastewater Flow Control No. 227B Filter No. 220B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FWCV-237A | Valve - Wastewater Flow Control No. 237A Filter No. 230A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FWCV-237B | Valve - Wastewater Flow Control No. 237B Filter No. 230B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FWCV-247A | Valve - Wastewater Flow Control No. 247A Filter No. 240A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
FWCV-247B | Valve - Wastewater Flow Control No. 247B Filter No. 240B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 22500 | 0.00099927 | 0.015738 | 0.00088282 | 0.013904
BFV-510 | Valve - EQ Pump No. 510 Isolation | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
BFV-520 | Valve - EQ Pump No. 520 Isolation | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
CV-510 | Valve - EQ Pump No. 510 Check | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
CV-520A | Valve - EQ Pump No. 520 Check A | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
CV-520B | Valve - EQ Pump No. 520 Check B | Pipe Gallery | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
M-EBP-510 | Motor - EQ Pump No. 510 | Pipe Gallery | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 11 | 30000 | 0.0013324 | 0.014656 | 0.0011771 | 0.012948
M-EBP-520 | Motor - EQ Pump No. 520 | Pipe Gallery | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 11 | 30000 | 0.0013324 | 0.014656 | 0.0011771 | 0.012948
P-EBP-510 | Pump No. 510 | Pipe Gallery | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 225000 | 0.0099927 | 0.19486 | 0.0088282 | 0.17215
P-EBP-520 | Pump No. 520 | Pipe Gallery | WAUL | CP | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 37.5 | 19.5 | 225000 | 0.0099927 | 0.19486 | 0.0088282 | 0.17215
P-LIM-71 | Pump - Lime Feed Metering No. 71 | Lime Room | WAUL | PP | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 37500 | 0.0016654 | 0.01832 | 0.0014714 | 0.016185
P-LIM-72 | Pump - Lime Feed Metering No. 72 | Lime Room | WAUL | PP | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 37500 | 0.0016654 | 0.01832 | 0.0014714 | 0.016185
P-LIM-72 | Pump - Lime Feed Metering No. 73 | Lime Room | WAUL | PP | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 37500 | 0.0016654 | 0.01832 | 0.0014714 | 0.016185
P-LIM-75 | Pump - Lime Feed Metering No. 75 | Lime Room | WAUL | PP | 20 | 2005 | 18 | 10% | Run time significantly less than expected | 15% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 32 | 14 | 37500 | 0.0016654 | 0.023316 | 0.0014714 | 0.020599
ER-ACU-01 | Air Conditioning Unit | Electrical Room | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 21.75 | 3.75 | 45000 | 0.0019985 | 0.0074945 | 0.0017656 | 0.0066212
MCC-1 | MCC-1 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 750000 | 0.033309 | 0.84938 | 0.029427 | 0.7504
VFD-P-320 | VFD - Pump No. 320 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 150000 | 0.0066618 | 0.16988 | 0.0058855 | 0.15008
VFD-P-310 | VFD - Pump No. 310 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 150000 | 0.0066618 | 0.16988 | 0.0058855 | 0.15008
VFD-P-310 | VFD - Pump No. 330 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 150000 | 0.0066618 | 0.16988 | 0.0058855 | 0.15008
VFD-P-310 | VFD - Pump No. 340 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 150000 | 0.0066618 | 0.16988 | 0.0058855 | 0.15008
RTCP-SCADA-PNL | SCADA Panel - Remote Telemetry | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 22.5 | 75000 | 0.0033309 | 0.074945 | 0.0029427 | 0.066212
SWB-MV-1 | Switchgear | Electrical Room | WAUL | EE | 30 | 2004 | 19 | 36.67% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 24.5 | 525000 | 0.023316 | 0.57125 | 0.020599 | 0.50468
MCC-1 | Transformer - MCC-1 | Electrical Room | WAUL | TX | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 30000 | 0.0013324 | 0.024316 | 0.0011771 | 0.021482
MCC-1 | Transformer - PP3 | Electrical Room | WAUL | TX | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
MCC-1 | Transformer - LP1 | Electrical Room | WAUL | TX | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
COMP-02 | Compressor No. 2 | Mechanical Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
EVP-1-COMP | Dryer - Service Air No. 1 | Mechanical Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
EVP-2-COMP | Dryer - Service Air No. 2 | Mechanical Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
COMP-01 | Compressor No. 1 | Mechanical Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
BLW-281 | Blower - Backwash Air No. 281 | Mechanical Room | WAUL | BL | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Very Good Condition | 25% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
BLW-282 | Blower - Backwash Air No. 282 | Mechanical Room | WAUL | BL | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Very Good Condition | 25% | 33.75 | 15.75 | 52500 | 0.0023316 | 0.036723 | 0.0020599 | 0.032444
CV-BLWA-281 | Valve - Blower No. 281 Check | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 12000 | 0.00053294 | 0.0097262 | 0.00047084 | 0.0085928
CV-BLWA-282 | Valve - Blower No. 282 Check | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 36.25 | 18.25 | 12000 | 0.00053294 | 0.0097262 | 0.00047084 | 0.0085928
FIT-280 | Flowmeter - Backwash Air | Mechanical Room | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 30000 | 0.0013324 | 0.0049963 | 0.0011771 | 0.0044141
M-BLW-281 | Motor - Blower No. 281 | Mechanical Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
M-BLW-282 | Motor - Blower No. 282 | Mechanical Room | WAUL | MO | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 29 | 11 | 7500 | 0.00033309 | 0.003664 | 0.00029427 | 0.003237
T-AIR-01 | Tank - Compressed Service Air | Mechanical Room | WAUL | TK | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 7500 | 0.00033309 | 0.0060789 | 0.00029427 | 0.0053705
GWH-01 | Hot Water Heater | Mechanical Room | WAUL | HV | 15 | 2014 | 9 | 40% | Run time is within expected range | 0% | Largely preventative maintenance | 10% | Very Good Condition | 25% | 20.25 | 11.25 | 15000 | 0.00066618 | 0.0074945 | 0.00058855 | 0.0066212
CLAR-210 | Clarifier No. 210 | Filter Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 750000 | 0.033309 | 0.3664 | 0.029427 | 0.3237
CLAR-220 | Clarifier No. 220 | Filter Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 750000 | 0.033309 | 0.3664 | 0.029427 | 0.3237
CLAR-230 | Clarifier No. 230 | Filter Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 29 | 11 | 750000 | 0.033309 | 0.3664 | 0.029427 | 0.3237
CLAR-240 | Clarifier No. 240 | Filter Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 11 | 750000 | 0.033309 | 0.3664 | 0.029427 | 0.3237
FILT-210A | Filter No. 210A | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-210B | Filter No. 210B | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-220A | Filter No. 220A | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-220B | Filter No. 220B | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-230A | Filter No. 230A | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-230B | Filter No. 230B | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-240A | Filter No. 240A | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FILT-240B | Filter No. 240B | Filter Room | WAUL | FI | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 750000 | 0.033309 | 0.12491 | 0.029427 | 0.11035
FCV-BWA-280 | Valve - Backwash Air Flow Control | Mechanical Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 15000 | 0.00066618 | 0.012158 | 0.00058855 | 0.010741
MAU-02 | Air Handling Unit - MAU-02 | Roof No. 1 | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 21.75 | 2.75 | 75000 | 0.0033309 | 0.0091599 | 0.0029427 | 0.0080925
MAU-02 | Air Handling Unit - MAU-01 | Roof No. 1 | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 21.75 | 3.75 | 75000 | 0.0033309 | 0.012491 | 0.0029427 | 0.011035
MAU-03 | Air Handling Unit - MAU-03 | Roof No. 1 | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 21.75 | 3.75 | 75000 | 0.0033309 | 0.012491 | 0.0029427 | 0.011035
MAU-04 | Air Handling Unit - MAU-04 | Roof No. 1 | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 25% | 21.75 | 2.75 | 75000 | 0.0033309 | 0.0091599 | 0.0029427 | 0.0080925
MAU-05 | Air Handling Unit - MAU-05 | Roof No. 2 | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 21.75 | 2.75 | 75000 | 0.0033309 | 0.0091599 | 0.0029427 | 0.0080925
PWSB-AHU-01 | Compressor/Condenser - Electrical Room AC | Roof No. 3 | WAUL | HV | 15 | 2018 | 5 | 66.67% | Run time is within expected range | 0% | Easily maintained | 10% | Very Good Condition | 0% | 16.5 | 11.5 | 45000 | 0.0019985 | 0.022983 | 0.0017656 | 0.020305
PWSB-AHU-02 | Mini Split - Office Compressor/Condenser | Roof No. 2 | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 2.75 | 15000 | 0.00066618 | 0.001832 | 0.00058855 | 0.0016185
PWSB-AHU-03 | Mini Split - Control Room Compressor/Condenser | Roof No. 3 | WAUL | HV | 15 | 2018 | 5 | 66.67% | Run time is within expected range | 0% | Easily maintained | 10% | Very Good Condition | 0% | 16.5 | 11.5 | 15000 | 0.00066618 | 0.007661 | 0.00058855 | 0.0067683
MAU-06 | Air Handling Unit - MAU-06 | Roof No. 3 | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Unserviceable | 0% | 18 | 0 | 75000 | 0.0033309 | 0 | 0.0029427 | 0
MAU-07 | Air Handling Unit - MAU-07 | Roof No. 3 | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 21.75 | 2.75 | 75000 | 0.0033309 | 0.0091599 | 0.0029427 | 0.0080925
SWB-MV-1 | Switchgear | Exterior | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 22.5 | 375000 | 0.016654 | 0.37473 | 0.014714 | 0.33106
- | Transformer |  | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 22.5 | 150000 | 0.0066618 | 0.14989 | 0.0058855 | 0.13242
ADMINISTRATIVE BUIDING
- | Air Handling Unit No. 1 |  | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 75000 | 0.0033309 | 0.012491 | 0.0029427 | 0.011035
- | Air Handling Unit No. 3 |  | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 75000 | 0.0033309 | 0.012491 | 0.0029427 | 0.011035
- | Air Handling Unit No. 2 |  | WAUL | HV | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 3.75 | 75000 | 0.0033309 | 0.012491 | 0.0029427 | 0.011035
RAW WATER OPERATIONS BUILDING
VAC-P-01 | Vacuum Pump - Inlet Pump Priming System No. 1 | Pump Room | WAUL | PE | 20 | 2004 | 19 | 5% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 10 | 7500 | 0.0025253 | 0.025253 | 0.00029427 | 0.0029427
VAC-P-02 | Vacuum Pump - Inlet Pump Priming System No. 2 | Pump Room | WAUL | PE | 20 | 2004 | 19 | 5% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 10 | 7500 | 0.0025253 | 0.025253 | 0.00029427 | 0.0029427
Generator unit | Generator | Exterior | WAUL | GN | 35 | 1995 | 28 | 20% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 15% | 47.25 | 19.25 | 300000 | 0.10101 | 1.9444 | 0.011771 | 0.22659
RW-VFD-P-111 | MCC-2 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 300000 | 0.10101 | 2.5758 | 0.011771 | 0.30016
RWPS-COMP-01 | Compressor - Hydroburst Air Supply | Pump Room | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 11 | 22500 | 0.0075758 | 0.083333 | 0.00088282 | 0.009711
BFV-110 | Valve - Raw Water Pump No. 110 Suction | Pump Room | WAUL | VA | 25 | 2004 | 19 | 24% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 14.75 | 30000 | 0.010101 | 0.14899 | 0.0011771 | 0.017362
BFV-120 | Valve - Raw Water Pump No. 120 Suction | Pump Room | WAUL | VA | 25 | 2004 | 19 | 24% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 14.75 | 30000 | 0.010101 | 0.14899 | 0.0011771 | 0.017362
FV-130 | Valve - Raw Water Pump No. 130 Discharge | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
FV-110 | Valve - Raw Water Pump No. 110 Discharge | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
FV-120 | Valve - Raw Water Pump No. 120 Discharge | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
BFV-130 | Valve - Raw Water Pump No. 130 Suction | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Some Defects and Deterioration | 15% | 33.75 | 15.75 | 30000 | 0.010101 | 0.15909 | 0.0011771 | 0.018539
CV-110 | Valve - Raw Water Pump No. 110 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
CV-120 | Valve - Raw Water Pump No. 120 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
CV-130 | Valve - Raw Water Pump No. 130 Check | Pump Room | WAUL | VA | 25 | 2005 | 18 | 28% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 36.25 | 18.25 | 30000 | 0.010101 | 0.18434 | 0.0011771 | 0.021482
FE-201 | Flow Element - Raw Water | Pump Room | WAUL | IC | 15 | 2005 | 18 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 21.75 | 3.75 | 67500 | 0.022727 | 0.085227 | 0.0026485 | 0.0099317
M-RWP-120 | HVAC Unit | Pump Room | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 2.75 | 75000 | 0.025253 | 0.069444 | 0.0029427 | 0.0080925
RW-VFD-P-110 | VFD - Raw Water Pump No. 110 | Electrical Room | WAUL | VD | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 29 | 11 | 37500 | 0.012626 | 0.13889 | 0.0014714 | 0.016185
M-RWP-130 | Motor - Raw Water Pump No. 130 | Pump Room | WAUL | MO | 20 | 2004 | 19 | 5% | Run time is more than expected | -10% | Easily maintained | 20% | Minor Defects Only | 25% | 27 | 8 | 30000 | 0.010101 | 0.080808 | 0.0011771 | 0.0094168
RW-VFD-P-111 | VFD - Raw Water Pump No. 130 | Electrical Room | WAUL | VD | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 29 | 11 | 37500 | 0.012626 | 0.13889 | 0.0014714 | 0.016185
M-RWP-120 | Motor - Raw Water Pump No. 120 | Pump Room | WAUL | MO | 20 | 2004 | 19 | 5% | Run time significantly less than expected | 15% | Easily maintained | 20% | Minor Defects Only | 25% | 32 | 13 | 30000 | 0.010101 | 0.13131 | 0.0011771 | 0.015302
M-RWP-110 | Motor - Raw Water Pump No. 110 | Pump Room | WAUL | MO | 20 | 2004 | 19 | 5% | Run time is more than expected | -10% | Easily maintained | 20% | Minor Defects Only | 25% | 27 | 8 | 30000 | 0.010101 | 0.080808 | 0.0011771 | 0.0094168
RWPS-HYDRO | Hydroburst - Intake Screen | Exterior | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 11 | 60000 | 0.020202 | 0.22222 | 0.0023542 | 0.025896
P-RWP-110 | Pump - Raw Water No. 110 | Pump Room | WAUL | CP | 30 | 2004 | 19 | 36.67% | Run time is more than expected | -10% | Easily maintained | 20% | Minor Defects Only | 15% | 37.5 | 18.5 | 225000 | 0.075758 | 1.4015 | 0.0088282 | 0.16332
P-RWP-130 | Pump - Raw Water No. 130 | Pump Room | WAUL | CP | 30 | 2004 | 19 | 36.67% | Run time is more than expected | -10% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 34.5 | 15.5 | 225000 | 0.075758 | 1.1742 | 0.0088282 | 0.13684
P-RWP-120 | Pump - Raw Water No. 120 | Pump Room | WAUL | CP | 30 | 2004 | 19 | 36.67% | Run time significantly less than expected | 15% | Largely preventative maintenance | 10% | Minor Defects Only | 15% | 42 | 23 | 225000 | 0.075758 | 1.7424 | 0.0088282 | 0.20305
RAD-STRIPPER-01 | Aerator No. 1 | Exterior | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 29 | 11 | 75000 | 0.025253 | 0.27778 | 0.0029427 | 0.03237
RAD-STRIPPER-01 | Aerator | Aerator Room | WAUL | PE | 20 | 1995 | 28 | 0% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Minor Defects Only | 25% | 29 | 1 | 30000 | 0.010101 | 0.010101 | 0.0011771 | 0.0011771
RAD-STRIPPER-01 | Aerator No. 2 | Exterior | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Largely preventative maintenance | 20% | Some Defects and Deterioration | 25% | 29 | 11 | 75000 | 0.025253 | 0.27778 | 0.0029427 | 0.03237
RW-SCADA-PNL | SCADA Panel | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 22.5 | 45000 | 0.015152 | 0.34091 | 0.0017656 | 0.039727
SLD-G-01 | Slide Gate - Lagoon No. 1 | Waste Process Area | WAUL | SG | 30 | 2004 | 19 | 36.67% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 15% | 40.5 | 21.5 | 30000 | 0.010101 | 0.21717 | 0.0011771 | 0.025308
SLD-G-02 | Slide Gate - Lagoon No. 2 | Waste Process Area | WAUL | PE | 20 | 2005 | 18 | 10% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 11 | 30000 | 0.010101 | 0.11111 | 0.0011771 | 0.012948
SCREEN-BOX-ASSBLY | Intake Screen - Raw Water | Exterior | WAUL | PE | 20 | 2004 | 19 | 5% | Run time is within expected range | 0% | Easily maintained | 20% | Minor Defects Only | 25% | 29 | 10 | 30000 | 0.010101 | 0.10101 | 0.0011771 | 0.011771
- | Lagoons | Waste Process Area | WAUL | GS | 300 | 2005 | 18 | 94% | Run time is within expected range | 0% | Largely preventative maintenance | -20% | Very Good Condition | 0% | 240 | 222 | 150000 | 0.050505 | 11.2121 | 0.0058855 | 1.3066
- | Piping | Pump Room | WAUL | PI | 50 | 2004 | 19 | 62% | Run time is within expected range | 0% | Easily maintained | 10% | Some Defects and Deterioration | 0% | 55 | 36 | 450000 | 0.15152 | 5.4545 | 0.017656 | 0.63563
- | Soft Starter - Raw Water Pump No. 120 | Electrical Room | WAUL | EE | 30 | 2005 | 18 | 40% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 43.5 | 25.5 | 30000 | 0.010101 | 0.25758 | 0.0011771 | 0.030016
- | HVAC Unit | Electrical Room | WAUL | HV | 15 | 2004 | 19 | 0% | Run time is within expected range | 0% | Easily maintained | 20% | Very Good Condition | 25% | 21.75 | 2.75 | 75000 | 0.025253 | 0.069444 | 0.0029427 | 0.0080925
| Main Plant Weighted Average Useful Life | [15 empty] | 22516500 |  | 14.7575
| Raw Water Weighted Average Useful Life | [15 empty] | 2970000 |  | 29.8125
| Total Weighted Average Useful Life | [15 empty] | 25486500 |  |  |  | 16.5119
STRUCTURES
WATER TREATMENT PLANT
- | Electrical Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Work Shop |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Equalization Basin No. 1 |  | Structural |  |  | 2005 | [15 empty] | 2
- | Sample Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Pump Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Lime Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Pipe Gallery |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Clearwell |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Mechanical Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Filter Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Control Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Work Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Process Building |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Stairway No. 1 |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Mechanical Corridor |  | Structural |  |  | 2005 | [15 empty] | 2
- | Chlorine Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Storage Closet |  | Structural |  |  | 2005 | [15 empty] | 2
- | Caustic Soda Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Ortho/Ammonium Sulfate Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Stairway No. 2 |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Equalization Basin No. 2 |  | Structural |  |  | 2005 | [15 empty] | 2
- | Hallway |  | Structural |  |  | 2005 | [15 empty] | 2
RAW WATER OPERATIONS BUILDING
- | Aerator Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Pump Room |  | Structural |  |  | 2005 | [15 empty] | 2.5
- | Electrical Room |  | Structural |  |  | 2005 | [15 empty] | 2
- | Raw Water Operations Building |  | Structural |  |  | 2005 | [15 empty] | 2