## 87 Branch
|  |  | 87 Branch Street KW Demand |  | Old | 7,809,000 KWh/Yr | 1657 | KWh/MG |  | HSP VFD's operational June 5, 2010
|  |  | 118 Mill Street KW Demand |  | New | 7,472,863 KWh/Yr | 1586 | KWh/MG |  | RWPS VFD's operational December 3, 2014
Starting Date | Ending Date | Kilo Watts | 12 Month Running Total KW | Average GPD | System Pumpage/MG | KW Per Million | Percentage +/- KWh/MG
2008-03-12 | 2008-04-10 | 637200 | [6 empty] | 2008-2009 | Bill Total | kWh | cost per kWh | 2009-2010 | Bill Total | kWh | cost per kWh | 2010-2011 | Bill Total | kWh | cost per kWh | 2011-2012 | Bill Total | kWh | cost per kWh
2008-04-11 | 2008-05-08 | 722100 |  | 8843107.1429 | 247.607 | 2916.315 | 83.88%
2008-05-09 | 6/9//2008 | 824600 |  | 10047781.25 | 321.529 | 2564.6209 | 61.7% |  | Mar | 86748.16 | 637200 | 0.13614 | Mar | 112995.47 | 801100 | 0.14105 | Mar | 114558.11 | 833600 | 0.13743 | Mar | 75087.59 | 523900 | 0.14332
2008-06-10 | 2008-07-08 | 848600 |  | 11445586.2069 | 331.922 | 2556.6247 | 61.2% |  | Apr | 97398.9 | 722100 | 0.13488 | Apr | 106877.56 | 742600 | 0.14392 | Apr | 105501.57 | 761600 | 0.13853 | Apr | 81291.83 | 570100 | 0.14259
2008-07-09 | 2008-08-07 | 883200 |  | 12065633.3333 | 361.969 | 2439.988 | 53.85% |  | May | 110218.44 | 824600 | 0.13366 | May | 110769.74 | 783400 | 0.1414 | May | 104406.96 | 749600 | 0.13928 | May | 87689.7 | 615900 | 0.14238
2008-08-08 | 2008-09-09 | 850500 |  | 10032181.8182 | 331.062 | 2569.0052 | 61.98% |  | Jun | 113332.39 | 848600 | 0.13355 | Jun | 115915.38 | 819700 | 0.14141 | Jun | 115538.57 | 841900 | 0.13724 | Jun | 87394.64 | 618700 | 0.14126
2008-09-10 | 2008-10-07 | 701300 |  | 8831464.2857 | 247.281 | 2836.0448 | 78.82% |  | Jul | 143662.34 | 883200 | 0.16266 | Jul | 111297.98 | 779000 | 0.14287 | Jul | 95562.7 | 684700 | 0.13957 | Jul | 95733.7 | 678400 | 0.14112
2008-10-08 | 2008-11-06 | 752200 |  | 8515333.3333 | 255.46 | 2944.4923 | 85.66% |  | Aug | 143759.03 | 850500 | 0.16903 | Aug | 119063.98 | 824600 | 0.14439 | Aug | 94863.34 | 688200 | 0.13784 | Aug | 80879.06 | 575200 | 0.14061
2008-11-07 | 2008-12-09 | 883600 |  | 7873939.3939 | 259.84 | 3400.5542 | 114.4% |  | Sep | 118365.97 | 701300 | 0.16878 | Sep | 124890.79 | 889600 | 0.14039 | Sep | 74996.62 | 536800 | 0.13971 | Sep | 78269.56 | 542500 | 0.14428
2008-12-10 | 2009-01-12 | 868500 |  | 7710911.7647 | 262.171 | 3312.7234 | 108.9% |  | Oct | 126484.35 | 752200 | 0.16815 | Oct | 98013.89 | 688200 | 0.14242 | Oct | 72147.45 | 504300 | 0.14306 | Oct | 77872.36 | 536900 | 0.14504
2009-01-13 | 2009-02-09 | 724100 |  | 8010464.2857 | 224.293 | 3228.3665 | 103.6% |  | Nov | 147522.7 | 883600 | 0.16696 | Nov | 114807.37 | 814000 | 0.14104 | Nov | 75304.93 | 535400 | 0.14065 | Nov | 84959.1 | 598100 | 0.14205
2009-02-10 | 2009-03-11 | 780300 | 9476200 | 7682433.3333 | 230.473 | 3385.646 | 113.5% |  | Dec | 135780.18 | 868500 | 0.15634 | Dec | 122835.95 | 872700 | 0.14075 | Dec | 78302.23 | 561800 | 0.13938 | Dec | 57745.76 | 539700 | 0.107
2009-03-12 | 2009-04-12 | 801100 | 9640100 | 7732593.75 | 247.443 | 3237.5133 | 104.1% |  | Jan | 100971.46 | 724100 | 0.13944 | Jan | 109828.18 | 766300 | 0.14332 | Jan | 71316.39 | 498300 | 0.14312 | Jan | 54203.19 | 513500 | 0.10556
2009-04-13 | 5/11/25009 | 742600 | 9660600 | 8553172.4138 | 248.042 | 2993.8478 | 88.77% |  | Feb | 108058.01 | 780300 | 0.13848 | Feb | 109142.16 | 784800 | 0.13907 | Feb | 69786.66 | 490100 | 0.14239 | Feb | 58903.5 | 545800 | 0.10792
2009-05-12 | 2009-06-10 | 783400 | 9619400 | 9444233.3333 | 283.327 | 2765.003 | 74.34%
2009-06-11 | 2009-07-13 | 819700 | 9590500 | 8557060.6061 | 282.383 | 2902.7951 | 83.03% |  | Average cost per kWh |  |  | 0.15067 | Average cost per kWh |  |  | 0.14184 | Average cost per kWh |  |  | 0.13985 | Average cost per kWh |  |  | 0.13359
2009-07-14 | 2009-08-11 | 779000 | 9486300 | 9321724.1379 | 270.33 | 2881.6632 | 81.69%
2009-08-12 | 2009-09-09 | 824600 | 9460400 | 10624206.8966 | 308.102 | 2676.3864 | 68.75%
2009-09-10 | 2009-10-11 | 889600 | 9648700 | 8829500 | 282.544 | 3148.5362 | 98.52%
2009-10-12 | 2009-11-08 | 688200 | 9584700 | 8156821.4286 | 228.391 | 3013.2536 | 89.99% |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost
2009-11-09 | 2009-12-09 | 814000 | 9515100 | 7547645.1613 | 233.977 | 3478.9744 | 119.4% |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh
2009-12-10 | 2010-01-11 | 872700 | 9519300 | 7685121.2121 | 253.609 | 3441.1239 | 117% |  | 2003337 | 301849.9295 |  |  | 2093137 | 296884.0881 |  |  | 213437 | 29849.1423 |  |  | 0 | 0
2010-01-12 | 2010-02-09 | 766300 | 9561500 | 7846535.7143 | 227.457 | 3368.9884 | 112.4%
2010-02-10 | 2010-03-11 | 784800 | 9566000 | 7575400 | 227.262 | 3453.283 | 117.7%
2010-03-12 | 2010-04-12 | 833600 | 9598500 | 7763343.75 | 248.427 | 3355.5129 | 111.6%
2010-04-13 | 2010-05-11 | 761600 | 9617500 | 8168379.3103 | 236.883 | 3215.0893 | 102.7% |  | 2012-2013 | Bill Total | kWh | cost per kWh | 2013-2014 | Bill Total | kWh | cost per kWh | 2014-2015 | Bill Total | kWh | cost per kWh | 2015-2016 | Bill Total | kWh | cost per kWh
2010-05-12 | 2010-06-09 | 749600 | 9583700 | 9702620.6897 | 281.376 | 2664.0509 | 67.97%
2010-06-10 | 2010-07-13 | 841900 | 9605900 | 10771705.8824 | 366.238 | 2298.7784 | 44.94% |  | Mar | 48968.21 | 470500 | 0.10408 | Mar | 52371.74 | 479700 | 0.10918 | Mar | 59162.05 | 514200 | 0.11506 | Mar | 69473.53 | 504500 | 0.13771
2010-07-14 | 2010-08-11 | 684700 | 9511600 | 10802896.5517 | 313.284 | 2185.5569 | 37.8% |  | Apr | 51305.27 | 487300 | 0.10528 | Apr | 63463.18 | 580800 | 0.10927 | Apr | 62409.89 | 551000 | 0.11327 | Apr | 66423.34 | 478700 | 0.13876
2010-08-12 | 2010-09-12 | 688200 | 9375200 | 10148531.25 | 324.753 | 2119.149 | 33.62% |  | May | 60129.9 | 574500 | 0.10466 | May | 66999.66 | 590800 | 0.1134 | May | 64690.23 | 573000 | 0.1129 | May | 91478.98 | 675700 | 0.13538
2010-09-13 | 2010-10-11 | 536800 | 9022400 | 8584068.9655 | 248.938 | 2156.3602 | 35.96% |  | Jun | 65023.33 | 612200 | 0.10621 | Jun | 68428.02 | 617600 | 0.1108 | Jun | 74942.12 | 675200 | 0.11099 | Jun | 85320.06 | 630500 | 0.13532
2010-10-12 | 2010-11-08 | 504300 | 8838500 | 7859407.4074 | 220.017 | 2292.0956 | 44.52% |  | Jul | 64338.03 | 620700 | 0.10365 | Jul | 79929.07 | 705000 | 0.11337 | Jul | 67273.61 | 600300 | 0.11207 | Jul | 82432.26 | 598000 | 0.13785
2010-11-09 | 2010-12-09 | 535400 | 8559900 | 7228838.7097 | 224.094 | 2389.176 | 50.64% |  | Aug | 64548.59 | 622600 | 0.10368 | Aug | 72254.07 | 617200 | 0.11707 | Aug | 66152.52 | 582700 | 0.11353 | Aug | 81494.88 | 589000 | 0.13836
2010-12-10 | 2011-01-10 | 561800 | 8249000 | 7136125 | 228.356 | 2460.1937 | 55.12% |  | Sep | 52130.57 | 483100 | 0.10791 | Sep | 61994.42 | 544400 | 0.11388 | Sep | 65016.76 | 577300 | 0.11262 | Sep | 63509.26 | 448100 | 0.14173
2011-01-11 | 2011-02-08 | 498300 | 7981000 | 7111896.5517 | 206.245 | 2416.0586 | 52.34% |  | Oct | 54205.15 | 509300 | 0.10643 | Oct | 60017.85 | 524100 | 0.11452 | Oct | 59471.52 | 533300 | 0.11152 | Oct | 64213.71 | 454300 | 0.14135
2011-02-09 | 2011-03-09 | 490100 | 7686300 | 7108931.0345 | 206.159 | 2377.2913 | 49.89% |  | Nov | 48646.09 | 456600 | 0.10654 | Nov | 67224.09 | 600300 | 0.11198 | Nov | 52837.25 | 467800 | 0.11295 | Nov | 60934.01 | 426600 | 0.14284
2011-03-10 | 2011-04-10 | 523900 | 7376600 | 6869375 | 219.82 | 2383.3136 | 50.27% |  | Dec | 52886.28 | 498400 | 0.10611 | Dec | 67914.88 | 607100 | 0.11187 | Dec | 65441.68 | 465600 | 0.14055 | Dec | 63454.32 | 449600 | 0.14114
2011-04-11 | 2011-05-10 | 570100 | 7185100 | 7966433.3333 | 238.993 | 2385.4255 | 50.41% |  | Jan | 57696.63 | 540700 | 0.10671 | Jan | 59588.71 | 522000 | 0.11415 | Jan | 63709.04 | 453300 | 0.14054 | Jan | 60842.44 | 417200 | 0.14584
2011-05-11 | 2011-06-09 | 615900 | 7051400 | 9502366.6667 | 285.071 | 2160.5144 | 36.22% |  | Feb | 52099.91 | 482900 | 0.10789 | Feb | 61428.29 | 536900 | 0.11441 | Feb | 66164.52 | 473100 | 0.13985 | Feb | 59516.53 | 414500 | 0.14359
2011-06-10 | 2011-07-11 | 618700 | 6828200 | 9029218.75 | 288.935 | 2141.3121 | 35.01%
2011-07-12 | 2011-08-10 | 678400 | 6821900 | 10530533.3333 | 315.916 | 2147.4063 | 35.4% |  | Average cost per kWh |  |  | 0.10576 | Average cost per kWh |  |  | 0.11283 | Average cost per kWh |  |  | 0.11965 | Average cost per kWh |  |  | 0.13999
2011-08-11 | 2011-09-11 | 575200 | 6708900 | 8077312.5 | 258.474 | 2225.3689 | 40.31%
2011-09-12 | 2011-10-10 | 542500 | 6714600 | 7052482.7586 | 204.522 | 2652.5264 | 67.25%
2011-10-11 | 2011-11-08 | 536900 | 6747200 | 6736241.3793 | 195.351 | 2748.3862 | 73.29%
2011-11-09 | 2011-12-11 | 598100 | 6809900 | 6382393.9394 | 210.619 | 2839.7248 | 79.05% |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost
2011-12-12 | 2012-01-10 | 539700 | 6787800 | 6217466.6667 | 186.524 | 2893.4614 | 82.44% |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh
2012-01-11 | 2012-02-08 | 513500 | 6803000 | 6209034.4828 | 180.062 | 2851.7955 | 79.81% |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2012-02-09 | 2012-03-11 | 545800 | 6858700 | 5814406.25 | 186.061 | 2933.4466 | 84.96%
2012-03-12 | 2012-04-10 | 470500 | 6805300 | 5927533.3333 | 177.826 | 2645.8448 | 66.83%
2012-04-11 | 2012-05-09 | 487300 | 6722500 | 6524931.0345 | 189.223 | 2575.2683 | 62.38%
2012-05-10 | 2012-06-11 | 574500 | 6681100 | 7186575.7576 | 237.157 | 2422.4459 | 52.74% |  | 2016-2017 | Bill Total | kWh | cost per kWh | 2017-2018 | Bill Total | kWh | cost per kWh | 2018-2019 | Bill Total | kWh | cost per kWh | 2019-2020 | Bill Total | kWh | cost per kWh
2012-06-12 | 2012-07-11 | 612200 | 6674600 | 8484866.6667 | 254.546 | 2405.0663 | 51.64%
2012-07-12 | 2012-08-09 | 620700 | 6616900 | 8965379.3103 | 259.996 | 2387.3444 | 50.53% |  | Mar | 66599.44 | 465700 | 0.14301 | Mar | 68295.18 | 443500 | 0.15399 | Mar | 57455.74 | 419100 | 0.13709 | Mar | 58991.81 | 419700 | 0.14056
2012-08-10 | 2012-09-11 | 622600 | 6664300 | 8106090.9091 | 267.501 | 2327.4679 | 46.75% |  | Apr | 67371.43 | 463400 | 0.14539 | Apr | 73798.22 | 462300 | 0.15963 | Apr | 59307.42 | 442000 | 0.13418 | Apr | 66655.59 | 481500 | 0.13843
2012-09-12 | 2012-10-10 | 483100 | 6604900 | 6998103.4483 | 202.945 | 2380.4479 | 50.09% |  | May | 81782.08 | 560700 | 0.14586 | May | 83719.22 | 541200 | 0.15469 | May | 70139.8 | 540900 | 0.12967 | May | 70263.88 | 516100 | 0.13614
2012-10-11 | 2012-11-06 | 509300 | 6577300 | 7331518.5185 | 197.951 | 2572.8589 | 62.22% | E (WTP) | Jun | 84315.39 | 586700 | 0.14371 | Jun | 85837.35 | 542900 | 0.15811 | Jun | 76584.23 | 582100 | 0.13157 | Jun | 70778.76 | 521600 | 0.1357
2012-11-07 | 2012-12-10 | 456600 | 6435800 | 6775882.3529 | 230.38 | 1981.9429 | 24.96% |  | Jul | 86440.05 | 593900 | 0.14555 | Jul | 78567.54 | 491000 | 0.16002 | Jul | 75296.84 | 571600 | 0.13173 | Jul | 82372.11 | 623300 | 0.13215
2012-12-11 | 2013-01-10 | 498400 | 6394500 | 6516193.5484 | 202.002 | 2467.3023 | 55.57% |  | Aug | 88985.5 | 617800 | 0.14404 | Aug | 96402.9 | 624900 | 0.15427 | Aug | 78215.8 | 586200 | 0.13343 | Aug | 73836.09 | 558000 | 0.13232
2013-01-11 | 2013-02-12 | 540700 | 6421700 | 7316216.7273 | 241.4352 | 2239.5248 | 41.21% | E (RWPS) | Sep | 74339.96 | 508900 | 0.14608 | Sep | 80615.73 | 512400 | 0.15733 | Sep | 69017.56 | 499500 | 0.13817 | Sep | 63035.03 | 469400 | 0.13429
2013-02-13 | 2013-03-11 | 482900 | 6358800 | 6869880.4815 | 185.4868 | 2603.4201 | 64.15% |  | Oct | 64148.97 | 428500 | 0.14971 | Oct | 73413.19 | 463900 | 0.15825 | Oct | 62900.82 | 445200 | 0.14129 | Oct | 63529.11 | 461200 | 0.13775
2013-03-12 | 2013-04-09 | 479700 | 6368000 | 6823103.4483 | 197.87 | 2424.319 | 52.86% |  | Nov | 72542.07 | 501300 | 0.14471 | Nov | 70173.7 | 447100 | 0.15695 | Nov | 66139.56 | 487300 | 0.13573 | Nov | 62947.36 | 466600 | 0.13491
2013-04-10 | 2013-05-12 | 580800 | 6461500 | 7523696.9697 | 248.282 | 2339.2755 | 47.5% |  | Dec | 65231.24 | 436300 | 0.14951 | Dec | 63796.89 | 461200 | 0.13833 | Dec | 63197.02 | 452700 | 0.1396 | Dec | 65039.69 | 480900 | 0.13525
2013-05-13 | 2013-06-11 | 590800 | 6477800 | 8911066.6667 | 267.332 | 2209.9861 | 39.34% |  | Jan | 66081.9 | 427600 | 0.15454 | Jan | 64701.04 | 464800 | 0.1392 | Jan | 61994.5 | 444700 | 0.13941 | Jan | 54630.75 | 392400 | 0.13922
2013-06-12 | 2013-07-11 | 617600 | 6483200 | 9248833.3333 | 277.465 | 2225.8663 | 40.34% |  | Feb | 63558.87 | 405000 | 0.15694 | Feb | 60392.9 | 440700 | 0.13704 | Feb | 64282.47 | 462900 | 0.13887 | Feb | 56355.79 | 407100 | 0.13843
2013-07-12 | 2013-08-13 | 705000 | 6567500 | 9771878.7879 | 322.472 | 2186.2363 | 37.85%
2013-08-14 | 2013-09-11 | 617200 | 6562100 | 9101620.6897 | 263.947 | 2338.3482 | 47.44% |  | Average cost per kWh |  |  | 0.14742 | Average cost per kWh |  |  | 0.15232 | Average cost per kWh |  |  | 0.13589 | Average cost per kWh |  |  | 0.13626
2013-09-12 | 2013-10-09 | 544400 | 6623400 | 8542892.8571 | 239.201 | 2275.9102 | 43.5%
2013-10-10 | 2013-11-06 | 524100 | 6638200 | 8082785.7143 | 226.318 | 2315.7681 | 46.01%
2013-11-07 | 2013-12-10 | 600300 | 6781900 | 7485882.3529 | 254.52 | 2358.5573 | 48.71%
2013-12-11 | 2014-01-12 | 607100 | 6890600 | 7700848.4848 | 254.128 | 2388.9536 | 50.63% |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost
2014-01-13 | 2014-02-10 | 522000 | 6871900 | 8023931.0345 | 232.694 | 2243.2895 | 41.44% |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh
2014-02-11 | 2014-03-11 | 536900 | 6925900 | 7970413.7931 | 231.142 | 2322.8145 | 46.46% |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2014-03-12 | 2014-04-09 | 514200 | 6960400 | 7854517.2414 | 227.781 | 2257.4315 | 42.33%
2014-04-10 | 2014-05-12 | 551000 | 6930600 | 7905000 | 260.865 | 2112.2036 | 33.18%
2014-05-13 | 2014-06-11 | 573000 | 6912800 | 9846733.3333 | 295.402 | 1939.7296 | 22.3%
2014-06-12 | 2014-07-13 | 675200 | 6970400 | 10957343.75 | 350.635 | 1925.6492 | 21.42% |  | 2020-2021 | Bill Total | kWh | cost per kWh | 2021-2022 | Bill Total | kWh | cost per kWh | 2022-2023 | Bill Total | kWh | cost per kWh | 2023-2024 | Bill Total | kWh | cost per kWh
2014-07-14 | 2014-08-12 | 600300 | 6865700 | 10315966.6667 | 309.479 | 1939.7116 | 22.3%
2014-08-13 | 2014-09-10 | 582700 | 6831200 | 10078310.3448 | 292.271 | 1993.6976 | 25.71% |  | Mar | 62991.1 | 446900 | 0.14095 | Mar | 68897.71 | 473100 | 0.14563 | Mar | 78111.79 | 436000 | 0.17916 | Mar | 98341.82 | 434400 | 0.22639
2014-09-11 | 2014-10-08 | 577300 | 6864100 | 10161285.7143 | 284.516 | 2029.0599 | 27.94% |  | Apr | 63723.47 | 433400 | 0.14703 | Apr | 65550 | 430200 | 0.15237 | Apr | 76990.59 | 418200 | 0.1841 | Apr | 92921.15 | 391100 | 0.23759
2014-10-09 | 2014-11-09 | 533300 | 6873300 | 8069062.5 | 258.21 | 2065.3731 | 30.23% |  | May | 68505.18 | 465700 | 0.1471 | May | 83100.05 | 568200 | 0.14625 | May | 96129.52 | 535900 | 0.17938 | May | 119436.58 | 512300 | 0.23314
2014-11-10 | 2014-12-10 | 467800 | 6740800 | 7257580.6452 | 224.985 | 2079.2497 | 31.1% |  | Jun | 90430.36 | 642000 | 0.14086 | Jun | 87257.43 | 596700 | 0.14623 | Jun | 108926.03 | 625500 | 0.17414 | Jun | 132536.79 | 569900 | 0.23256
2014-12-11 | 2015-01-12 | 465600 | 6599300 | 7148000 | 235.884 | 1973.8516 | 24.45% | E (RWPS) | Jul | 90942.82 | 624400 | 0.14565 | Jul | 91548.04 | 626100 | 0.14622 | Jul | 114327.41 | 655500 | 0.17441 | Jul | 160154.85 | 680400 | 0.23538
2015-01-13 | 2015-02-11 | 453300 | 6530600 | 7354600 | 220.638 | 2054.4965 | 29.54% |  | Aug | 87766.85 | 602300 | 0.14572 | Aug | 85812.12 | 571800 | 0.15007 | Aug | 111099.93 | 635400 | 0.17485 | Aug | 124979.71 | 504900 | 0.24753
2015-02-12 | 2015-03-12 | 473100 | 6466800 | 7972862.069 | 231.213 | 2046.1652 | 29.01% |  | Sep | 81453.64 | 550700 | 0.14791 | Sep | 81466.75 | 561900 | 0.14498 | Sep | 106128.32 | 611100 | 0.17367 | Sep | 133631.4 | 557200 | 0.23983
2015-03-13 | 2015-04-13 | 504500 | 6457100 | 8073000 | 258.336 | 1952.8831 | 23.13% |  | Oct | 78908.7 | 531600 | 0.14844 | Oct | 66156.4 | 438000 | 0.15104 | Oct | 75193.81 | 413100 | 0.18202 | Oct | 107496.68 | 441600 | 0.24343
2015-04-14 | 2015-05-11 | 478700 | 6384800 | 9066714.2857 | 253.868 | 1885.6256 | 18.89% | E (RWPS) | Nov | 76177.94 | 525000 | 0.1451 | Nov | 83839.63 | 484200 | 0.17315 | Nov | 77307.91 | 431600 | 0.17912 | Nov | 88538.49 | 459900 | 0.19252
2015-05-12 | 2015-06-10 | 675700 | 6487500 | 12616933.3333 | 378.508 | 1785.167 | 12.56% |  | Dec | 75077.21 | 515400 | 0.14567 | Dec | 84202.63 | 478600 | 0.17594 | Dec | 108636.48 | 464600 | 0.23383 | Dec |  |  | #DIV/0!
2015-06-11 | 2015-07-12 | 630500 | 6442800 | 11280187.5 | 360.966 | 1746.7019 | 10.13% | E (RWPS) | Jan | 65526.97 | 449800 | 0.14568 | Jan | 74207.19 | 416100 | 0.17834 | Jan | 98967.16 | 440500 | 0.22467 | Jan |  |  | #DIV/0!
2015-07-13 | 2015-08-11 | 598000 | 6440500 | 11491400 | 344.742 | 1734.6305 | 9.371% |  | Feb | 64915.14 | 438300 | 0.14811 | Feb | 73927.61 | 406500 | 0.18186 | Feb | 93463.84 | 417500 | 0.22387 | Feb |  |  | #DIV/0!
2015-08-12 | 2015-09-10 | 589000 | 6446800 | 10912400 | 327.372 | 1799.1765 | 13.44%
2015-09-11 | 2015-10-08 | 448100 | 6317600 | 8920214.2857 | 249.766 | 1794.0793 | 13.12% |  | Average cost per kWh |  |  | 0.14568 | Average cost per kWh |  |  | 0.15767 | Average cost per kWh |  |  | 0.19027 | Average cost per kWh |  |  | #DIV/0!
2015-10-09 | 2015-11-08 | 454300 | 6238600 | 7995096.7742 | 247.848 | 1832.9783 | 15.57%
2015-11-09 | 2015-12-09 | 426600 | 6197400 | 7250419.3548 | 224.763 | 1897.9992 | 19.67%
2015-12-10 | 2016-01-11 | 449600 | 6181400 | 7028757.5758 | 231.949 | 1938.3571 | 22.22%
2016-01-12 | 2016-02-08 | 417200 | 6145300 | 6970000 | 195.16 | 2137.7331 | 34.79% |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost |  |  | Excess | Cost
2016-02-09 | 2016-03-09 | 414500 | 6086700 | 7365833.3333 | 220.975 | 1875.7778 | 18.27% |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh |  |  |  | Power kWh
2016-03-10 | 2016-04-12 | 465700 | 6047900 | 7308411.7647 | 248.486 | 1874.1499 | 18.17% |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | #DIV/0!
2016-04-13 | 2016-05-11 | 463400 | 6032600 | 8485241.3793 | 246.072 | 1883.1887 | 18.74%
2016-05-12 | 2016-06-12 | 560700 | 5917600 | 9802687.5 | 313.686 | 1787.4562 | 12.7%
2016-06-13 | 2016-07-12 | 586700 | 5873800 | 10795733.3333 | 323.872 | 1811.5181 | 14.22%
2016-07-13 | 2016-08-10 | 593900 | 5869700 | 11418724.1379 | 331.143 | 1793.485 | 13.08%
2016-08-11 | 2016-09-12 | 617800 | 5898500 | 10191242.4242 | 336.311 | 1836.9902 | 15.83% | E (RWPS)
2016-09-13 | 2016-10-11 | 508900 | 5959300 | 9612482.7586 | 278.762 | 1825.5716 | 15.11% | E (RWPS)
2016-10-12 | 2016-11-07 | 428500 | 5933500 | 8448037.037 | 278.762 | 1537.1536 | -3.08% | E (RWPS)
2016-11-08 | 2016-12-11 | 501300 | 6008200 | 7466676.4706 | 253.867 | 1974.656 | 24.51% | E (RWPS)
2016-12-12 | 2017-01-10 | 436300 | 5994900 | 7404966.6667 | 222.149 | 1963.9971 | 23.83% | E (RWPS)
2017-01-11 | 2017-02-08 | 427600 | 6005300 | 7373172.4138 | 213.822 | 1999.7942 | 26.09%
2017-02-09 | 2017-03-09 | 405000 | 5995800 | 7119758.6207 | 206.473 | 1961.5155 | 23.68% | E (RWPS)
2017-03-10 | 2017-04-09 | 443500 | 5973600 | 7021096.7742 | 217.654 | 2037.6377 | 28.48%
2017-04-10 | 2017-05-09 | 462300 | 5972500 | 7623433.3333 | 228.703 | 2021.3989 | 27.45% | E (RWPS)
2017-05-10 | 2017-06-11 | 541200 | 5953000 | 8381181.8182 | 276.579 | 1956.7646 | 23.38%
2017-06-12 | 2017-07-11 | 542900 | 5909200 | 9746633.3333 | 292.399 | 1856.7095 | 17.07% | E (RWPS)
2017-07-12 | 2017-08-09 | 491000 | 5806300 | 9735241.3793 | 282.322 | 1739.1489 | 9.656% | E (RWPS)
2017-08-10 | 2017-09-11 | 624900 | 5813400 | 10087666.6667 | 332.893 | 1877.1798 | 18.36%
2017-09-12 | 2017-10-10 | 512400 | 5816900 | 9634758.6207 | 279.408 | 1833.8773 | 15.63%
2017-10-11 | 2017-11-08 | 463900 | 5852300 | 8106862.069 | 235.099 | 1973.2113 | 24.41% | E (RWPS & WTP)
2017-11-09 | 2017-12-10 | 447100 | 5798100 | 6984906.25 | 223.517 | 2000.2953 | 26.12%
2017-12-11 | 2018-01-10 | 461200 | 5823000 | 7363354.8387 | 228.264 | 2020.4675 | 27.39%
2018-01-11 | 2018-02-07 | 464800 | 5860200 | 7601357.1429 | 212.838 | 2183.8206 | 37.69%
2018-02-08 | 2018-03-11 | 440700 | 5895900 | 6799031.25 | 217.569 | 2025.5643 | 27.72%
2018-03-12 | 2018-04-09 | 419100 | 5871500 | 6906344.8276 | 200.284 | 2092.5286 | 31.94%
2018-04-10 | 2018-05-08 | 442000 | 5851200 | 7588068.9655 | 220.054 | 2008.5979 | 26.65%
2018-05-09 | 2018-06-11 | 540900 | 5850900 | 8266176.4706 | 281.05 | 1924.5686 | 21.35%
2018-06-12 | 2018-07-10 | 582100 | 5890100 | 10737827.5862 | 311.397 | 1869.3179 | 17.86%
2018-07-11 | 2018-08-08 | 571600 | 5970700 | 10549000 | 305.921 | 1868.4562 | 17.81%
2018-08-09 | 2018-09-09 | 586200 | 5932000 | 10790781.25 | 345.305 | 1697.6296 | 7.038%
2018-09-10 | 2018-10-10 | 499500 | 5919100 | 8718483.871 | 270.273 | 1848.1313 | 16.53%
2018-10-11 | 2018-11-06 | 445200 | 5900400 | 8082185.1852 | 218.219 | 2040.1523 | 28.64%
2018-11-07 | 2018-12-09 | 487300 | 5940600 | 7150424.2424 | 235.964 | 2065.1455 | 30.21%
2018-12-10 | 2019-01-09 | 452700 | 5932100 | 7013290.3226 | 217.412 | 2082.2218 | 31.29%
2019-01-10 | 2019-02-07 | 444700 | 5912000 | 7295793.1034 | 211.578 | 2101.8253 | 32.52%
2019-02-08 | 2019-03-10 | 462900 | 5934200 | 7158387.0968 | 221.91 | 2085.9808 | 31.52%
2019-03-11 | 2019-04-08 | 419700 | 5934800 | 7062103.4483 | 204.801 | 2049.3064 | 29.21%
2019-04-09 | 2019-05-09 | 481500 | 5974300 | 8189774.1935 | 253.883 | 1896.5429 | 19.58%
2019-05-10 | 2019-06-10 | 516100 | 5949500 | 8647750 | 276.728 | 1865.0082 | 17.59%
2019-06-11 | 2019-07-10 | 521600 | 5889000 | 9118633.3333 | 273.559 | 1906.7185 | 20.22%
2019-07-11 | 2019-08-12 | 623300 | 5940700 | 10284818.1818 | 339.399 | 1836.4815 | 15.79%
2019-08-13 | 2019-09-11 | 558000 | 5912500 | 9470466.6667 | 284.114 | 1964.0004 | 23.83%
2019-09-12 | 2019-10-08 | 469400 | 5882400 | 8360111.1111 | 225.723 | 2079.54 | 31.12%
2019-10-09 | 2019-11-06 | 461200 | 5898400 | 7365103.4483 | 213.588 | 2159.2973 | 36.15%
2019-11-07 | 2019-12-09 | 466600 | 5877700 | 6821212.1212 | 225.1 | 2072.8565 | 30.7%
2019-12-10 | 2020-01-12 | 480900 | 5905900 | 6855529.4118 | 233.088 | 2063.1693 | 30.09%
2020-01-13 | 2020-02-09 | 392400 | 5853600 | 6589642.8571 | 184.51 | 2126.714 | 34.09%
2020-02-10 | 2020-03-09 | 407100 | 5797800 | 6578517.2414 | 190.777 | 2133.905 | 34.55%
2020-03-10 | 2020-04-09 | 446900 | 5825000 | 7044387.0968 | 218.376 | 2046.4703 | 29.03%
2020-04-10 | 2020-05-10 | 433400 | 5776900 | 6788741.9355 | 210.451 | 2059.3867 | 29.85%
2020-05-11 | 2020-06-08 | 465700 | 5726500 | 8646275.8621 | 250.742 | 1857.2876 | 17.11%
2020-06-09 | 2020-07-12 | 642000 | 5846900 | 10867882.3529 | 369.508 | 1737.4455 | 9.549%
2020-07-13 | 2020-08-10 | 624400 | 5848000 | 11777413.7931 | 341.545 | 1828.1632 | 15.27%
2020-08-11 | 2020-09-08 | 602300 | 5892300 | 11304931.0345 | 327.843 | 1837.1599 | 15.84%
2020-09-09 | 2020-10-06 | 550700 | 5973600 | 10089607.1429 | 282.509 | 1949.3184 | 22.91%
2020-10-07 | 2020-11-05 | 531600 | 6044000 | 9366400 | 280.992 | 1891.8688 | 19.29%
2020-11-06 | 2020-12-09 | 525000 | 6102400 | 8460705.8824 | 287.664 | 1825.0459 | 15.07%
2020-12-10 | 2021-01-11 | 515400 | 6136900 | 8004787.8788 | 264.158 | 1951.105 | 23.02%
2021-01-12 | 2021-02-09 | 449800 | 6194300 | 7720965.5172 | 223.908 | 2008.8608 | 26.66%
2021-02-10 | 2021-03-10 | 438300 | 6225500 | 7276413.7931 | 211.016 | 2077.0937 | 30.96%
2021-03-11 | 2021-04-12 | 473100 | 6251700 | 7262545.4545 | 239.664 | 1974.0136 | 24.46%
2021-04-13 | 2021-05-10 | 430200 | 6248500 | 7563643.5714 | 211.782 | 2031.3339 | 28.08%
2021-05-11 | 2021-06-09 | 568200 | 6351000 | 9942846.6667 | 298.2854 | 1904.8871 | 20.11%
2021-06-10 | 2021-07-11 | 596700 | 6305700 | 9841050.625 | 314.9136 | 1894.8053 | 19.47%
2021-07-12 | 2021-08-10 | 626100 | 6307400 | 10163931 | 304.9179 | 2053.3394 | 29.47%
2021-08-11 | 2021-09-09 | 571800 | 6276900 | 9133929.6667 | 274.0179 | 2086.7251 | 31.57%
2021-09-10 | 2021-10-11 | 561900 | 6288100 | 7669125 | 245.412 | 2289.6191 | 44.36%
2021-10-12 | 2021-11-07 | 438000 | 6194500 | 7125851.8519 | 192.398 | 2276.5309 | 43.54%
2021-11-08 | 2021-12-08 | 484200 | 6153700 | 7572032.2581 | 234.733 | 2062.7692 | 30.06%
2021-12-09 | 2022-01-09 | 478600 | 6116900 | 6885968.75 | 220.351 | 2171.9892 | 36.95%
2022-01-10 | 2022-02-07 | 416100 | 6083200 | 6539758.6207 | 189.653 | 2194.0069 | 38.34%
2022-02-08 | 2022-03-09 | 406500 | 6051400 | 5964066.6667 | 178.922 | 2271.9397 | 43.25%
2022-03-10 | 2022-04-10 | 436000 | 6014300 | 6636375 | 212.364 | 2053.0787 | 29.45%
2022-04-11 | 2022-05-09 | 418200 | 6002300 | 6709068.9655 | 194.563 | 2149.4323 | 35.53%
2022-05-10 | 2000-06-08 | 535900 | 5970000 | 8679033.3333 | 260.371 | 2058.2169 | 29.77%
2022-06-09 | 2022-07-10 | 625500 | 5998800 | 9257968.75 | 296.255 | 2111.3568 | 33.12%
2022-07-11 | 2022-08-09 | 655500 | 6028200 | 10506466.6667 | 315.194 | 2079.6716 | 31.13%
2022-08-10 | 2022-09-08 | 635400 | 6091800 | 9207900 | 276.237 | 2300.1987 | 45.03%
2022-09-09 | 2022-10-11 | 611100 | 6141000 | 7823030.303 | 258.16 | 2367.1367 | 49.25%
2022-10-12 | 2022-11-07 | 413100 | 6116100 | 6606925.9259 | 178.387 | 2315.7517 | 46.01%
2022-11-08 | 2022-12-08 | 431600 | 6063500 | 6052516.129 | 187.628 | 2300.2963 | 45.04%
2022-12-09 | 2023-01-09 | 464600 | 6049500 | 6401937.5 | 204.862 | 2267.8681 | 42.99%
2023-01-10 | 2023-02-07 | 440500 | 6073900 | 6746034.4828 | 195.635 | 2251.6421 | 41.97%
2023-02-08 | 2023-03-09 | 417500 | 6084900 | 6084533.3333 | 182.536 | 2287.2201 | 44.21%
2023-03-10 | 2023-04-10 | 434400 | 6083300 | 5738000 | 183.616 | 2365.8069 | 49.17%
2023-04-11 | 2023-05-09 | 391100 | 6056200 | 6488000 | 188.152 | 2078.6385 | 31.06%
2023-05-10 | 2023-06-08 | 512300 | 6032600 | 7957966.6667 | 238.739 | 2145.858 | 35.3%
2023-06-09 | 2023-07-10 | 569900 | 5977000 | 9517677.4194 | 305.062 | 1868.1448 | 17.79%
2023-07-11 | 2023-08-15 | 680400 | 6001900 | 10037000 | 361.332 | 1883.0328 | 18.73%
2023-08-16 | 2023-09-10 | 504900 | 5871400 | 9014423.0769 | 234.375 | 2154.24 | 35.83%
2023-09-11 | 2023-10-09 | 557200 | 5817500 | 7908862.069 | 229.357 | 2429.4005 | 53.18%
2023-10-10 | 2023-11-07 | 441600 | 5846000 | 7320655.1724 | 212.299 | 2080.0852 | 31.15%
2023-11-08 | 2023-12-10 | 459900 | 5874300 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 5409700 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 4969200 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 4551700 | 0 | 0 | #DIV/0! | #DIV/0!

## yearly
Period | Kilo Watts 2008 | Kilo Watts 2009 | Kilo Watts 2010 | Kilo Watts 2011 | Kilo Watts 2012 | Kilo Watts 2013 | Kilo Watts 2014 | Kilo Watts 2015 | Kilo Watts 2016 | 6 year average
Mar | 637200 | 801100 | 833600 | 523900 | 470500 | 479700 | 514200 | 504500 | 465700 | 493083.3333
Apr | 722100 | 742600 | 761600 | 570100 | 487300 | 580800 | 551000 | 478700 | 463400 | 521883.3333
May | 824600 | 783400 | 749600 | 615900 | 574500 | 590800 | 573000 | 675700 | 560700 | 598433.3333
Jun | 848600 | 819700 | 841900 | 618700 | 612200 | 617600 | 675200 | 630500 | 586700 | 623483.3333
Jul | 883200 | 779000 | 684700 | 678400 | 620700 | 705000 | 600300 | 598000 | 593900 | 632716.6667
Aug | 850500 | 824600 | 688200 | 575200 | 622600 | 617200 | 582700 | 589000 | 617800 | 600750
Sep | 701300 | 889600 | 536800 | 542500 | 483100 | 544400 | 577300 | 448100 |  | 519080
Oct | 752200 | 688200 | 504300 | 536900 | 509300 | 524100 | 533300 | 454300 |  | 511580
Nov | 883600 | 814000 | 535400 | 598100 | 456600 | 600300 | 467800 | 426600 |  | 509880
Dec | 868500 | 872700 | 561800 | 539700 | 498400 | 607100 | 465600 | 449600 |  | 512080
Jan | 724100 | 766300 | 498300 | 513500 | 540700 | 522000 | 453300 | 417200 |  | 489340
Feb | 780300 | 784800 | 490100 | 545800 | 482900 | 536900 | 473100 | 414500 |  | 490640
YTD | 9476200 | 9566000 | 7686300 | 6858700 | 6358800 | 6925900 | 6466800 | 6086700 | 3288200

## trend
Period | Kilo Watts | year
Mar | 637200 | 2008
Apr | 722100
May | 824600
Jun | 848600
Jul | 883200
Aug | 850500
Sep | 701300
Oct | 752200
Nov | 883600
Dec | 868500
Jan | 724100
Feb | 780300
Mar | 801100 | 2009
Apr | 742600
May | 783400
Jun | 819700
Jul | 779000
Aug | 824600
Sep | 889600
Oct | 688200
Nov | 814000
Dec | 872700
Jan | 766300
Feb | 784800
Mar | 833600 | 2010
Apr | 761600
May | 749600
Jun | 841900
Jul | 684700
Aug | 688200
Sep | 536800
Oct | 504300
Nov | 535400
Dec | 561800
Jan | 498300
Feb | 490100
Mar | 523900 | 2011
Apr | 570100
May | 615900
Jun | 618700
Jul | 678400
Aug | 575200
Sep | 542500
Oct | 536900
Nov | 598100
Dec | 539700
Jan | 513500
Feb | 545800
Mar | 470500 | 2012
Apr | 487300
May | 574500
Jun | 612200
Jul | 620700
Aug | 622600
Sep | 483100
Oct | 509300
Nov | 456600
Dec | 498400
Jan | 540700
Feb | 482900
Mar | 479700 | 2013
Apr | 580800
May | 590800
Jun | 617600
Jul | 705000
Aug | 617200
Sep | 544400
Oct | 524100
Nov | 600300
Dec | 607100
Jan | 522000
Feb | 536900
Mar | 514200 | 2014
Apr | 551000
May | 573000
Jun | 675200
Jul | 600300
Aug | 582700
Sep | 577300
Oct | 533300
Nov | 467800
Dec | 528600

## power vs pump
Kilowatts Billing Period | Million Gallons Billing Period | Billing Period
722100 | 247.607 | Apr | 2008
824600 | 321.529 | May
848600 | 331.922 | Jun
883200 | 361.969 | Jul
850500 | 331.062 | Aug
701300 | 247.281 | Sep
752200 | 255.46 | Oct
883600 | 259.84 | Nov
868500 | 262.171 | Dec
724100 | 224.293 | Jan
780300 | 230.473 | Feb
801100 | 247.443 | Mar
742600 | 248.042 | Apr | 2009
783400 | 283.327 | May
819700 | 282.383 | Jun
779000 | 270.33 | Jul
824600 | 308.102 | Aug
889600 | 282.544 | Sep
688200 | 228.391 | Oct
814000 | 233.977 | Nov
872700 | 253.609 | Dec
766300 | 227.457 | Jan
784800 | 227.262 | Feb
833600 | 248.427 | Mar
761600 | 236.883 | Apr | 2010
749600 | 281.376 | May
841900 | 366.238 | Jun
684700 | 313.284 | Jul
688200 | 324.753 | Aug
536800 | 248.938 | Sep
504300 | 220.017 | Oct
535400 | 224.094 | Nov
561800 | 228.356 | Dec
498300 | 206.245 | Jan
490100 | 206.159 | Feb
523900 | 219.82 | Mar
570100 | 238.993 | Apr | 2011
615900 | 285.071 | May
618700 | 288.935 | Jun
678400 | 315.916 | Jul
575200 | 258.474 | Aug
542500 | 204.522 | Sep
536900 | 195.351 | Oct
598100 | 210.619 | Nov
539700 | 186.524 | Dec
513500 | 180.062 | Jan
545800 | 186.061 | Feb
470500 | 177.826 | Mar
487300 | 189.223 | Apr | 2012
574500 | 237.157 | May
612200 | 254.546 | Jun
620700 | 259.996 | Jul
622600 | 267.501 | Aug
483100 | 202.945 | Sep
509300 | 197.951 | Oct
456600 | 230.38 | Nov
498400 | 202.002 | Dec
540700 | 241.435 | Jan
482900 | 185.487 | Feb
479700 | 197.87 | Mar
580800 | 248.282 | Apr | 2013
590800 | 267.332 | May
617600 | 277.465 | Jun
705000 | 322.472 | Jul
617200 | 263.947 | Aug
544400 | 239.201 | Sep
524100 | 226.318 | Oct
600300 | 254.52 | Nov
607100 | 254.128 | Dec
522000 | 232.694 | Jan
536900 | 231.142 | Feb
514200 | 227.781 | Mar
551000 | 260.865 | Apr | 2014
573000 | 295.402 | May
675200 | 350.635 | Jun
600300 | 309.479 | Jul
582700 | 292.271 | Aug
577300 | 284.516 | Sep
533300 | 258.21 | Oct
467800 | 224.985 | Nov
528600 | 235.884 | Dec

## pumpage
Pumpage | 2008 | [8 empty] | 2009 | [11 empty] | 2010 | [11 empty] | 2011 | [11 empty] | 2012 | [11 empty] | 2013 | [11 empty] | 2014 | [11 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022 | [11 empty] | 2023
| 4/11-5/8 | 5/9-6/9 | 6/10-7/8 | 7/9-8/7 | 8/8-9/9 | 9/10-10/7 | 10/8-11/6 | 11/7-12/9 | 12/10-1/12 | 1/13-2/9 | 2/10-3/11 | 3/12-4/12 | 4/13-5/11 | 5/12-6/10 | 6/11-7/13 | 7/14-8/11 | 8/12-9/9 | 9/10-10/11 | 10/12-11/8 | 11/9-12/9 | 12/10-1/11 | 1/12-2/9 | 2/10-3/11 | 3/12-4/12 | 4/13-5/11 | 5/12-6/9 | 6/10-7/13 | 7/14-8/11 | 8/12-9/12 | 9/13-10/11 | 10/12-11/8 | 11/9-12/9 | 12/10-1/10 | 1/11-2/8 | 2/9-3/9 | 3/10-4/10 | 4/11-5/10 | 5/11-6/9 | 6/10-7/11 | 7/12-8/10 | 8/11-9/11 | 9/12-10/10 | 10/11-11/8 | 11/9-12/11 | 12/12-1/10 | 1/11-2/8 | 2/9-3/11 | 3/12-4/10 | 4/11-5/9 | 5/10-6/11 | 6/12-7/11 | 7/12-8/9 | 8/10-9/11 | 9/12-10/10 | 10/11-11/6 | 11/7-12/10 | 12/11-1/10 | 1/11-2/12 | 2/13-3/11 | 3/12-4/9 | 4/10-5/12 | 5/13-6/11 | 6/12-7/11 | 7/12-8/13 | 8/14-9/11 | 9/12-10/9 | 10/10-11/6 | 11/7-12/10 | 12/11-1/12 | 1/13-2/10 | 2/11-3/11 | 3/12-4/9 | 4/10-5/12 | 5/13-6/11 | 6/12-7/13 | 7/14-8/12 | 8/13-9/10 | 9/11-10/8 | 10/9-11/9 | 11/10-12/10 | 12/11-1/12 | 1/13-2/11 | 2/12-3/12 | 3/13-4/13 | 4/14-5/11 | 5/12-6/10 | 6/11-7/12 | 7/13-8/11 | 8/12-9/10 | 9/11-10/8 | 10/9-11/8 | 11/9-12/9 | 12/10-1/11 | 1/12-2/8 | 2/9-3/9 | 3/10-4/12 | 4/13-5/11 | 5/12-6/12 | 6/13-7/12 | 7/13-8/10 | 8/11-9/12 | 9/13-10/11 | 10/12-11/7 | 11/8-12/11 | 12/12-1/10 | 1/11-2/8 | 2/9-3/9 | 3/10-4/9 | 4/10-5/9 | 5/10-6/11 | 6/12-7/11 | 7/12-8/9 | 8/10-9/11 | 9/12-10/10 | 10/11-11/8 | 11/9-12/10 | 12/11-1/10 | 1/11-2/7 | 2/8-3/11 | 3/12-4/9 | 4/10-5/8 | 5/9-6/11 | 6/12-7/10 | 7/11-8/8 | 8/9-9/9 | 9/10-10/10 | 10/11-11/6 | 11/7-12/9 | 12/10-1/9 | 1/10-2/7 | 2/8-3/10 | 3/11-4/8 | 4/9-5/9 | 5/10-6/10 | 6/11-7/10 | 7/11-8/12 | 8/13-9/11 | 9/12-10/8 | 10/9-11/6 | 11/7-12/9 | 12/10-1/12 | 1/13-2/9 | 2/10-3/9 | 3/10-4/9 | 4/10-5/10 | 5/11-6/8 | 6/9-7/12 | 7/13-8/10 | 8/11-9/8 | 9/9-10/6 | 10/7-11/5 | 11/6-12/9 | 12/10-1/11 | 1/12-2/9 | 2/10-3/10 | 3/11-4/12 | 4/13-5/10 | 5/11-6/9 | 6/10-7/11 | 7/12-8/10 | 8/11-9/9 | 9/10-10/11 | 10/12-11/7 | 11/8-12/8 | 12/9-1/9 | 1/10-2/7 | 2/8-3/9 | 3/10-4/10 | 4/11-5/9 | 5/10-6/8 | 6/9-7/10 | 7/11-8/9 | 8/10-9/8 | 9/9-10/11 | 10/12-11/7 | 11/8-12/8 | 12/9-1/9 | 1/10-2/7 | 2/8-3/9 | 3/10-4/10 | 4/11-5/9 | 5/10-6/8 | 6/9-7/10 | 7/11-8/15 | 8/16-9/10 | 9/11-10/9 | 10/10-11/7 | 11/8-12/10
| 9030000 | 9275000 | 15458000 | 13101000 | 8683000 | 9161000 | 8786000 | 7907000 | 7894000 | 7441000 | 7951000 | 8330000 | 7998000 | 8821000 | 8849000 | 9100000 | 10719000 | 9929000 | 8204000 | 8136000 | 7303000 | 7754000 | 7823000 | 7314000 | 7867000 | 8800000 | 7744000 | 8992000 | 11086000 | 9001000 | 7813000 | 7907000 | 7384000 | 7026000 | 7023000 | 6987000 | 7431000 | 8922000 | 8694000 | 10547000 | 8221000 | 7346000 | 6616000 | 7553000 | 6294000 | 7075000 | 6539000 | 4891000 | 5466000 | 7292000 | 10921000 | 11485000 | 9479000 | 8224000 | 7419000 | 7607000 | 5724000 | 6712000 | 7489371 | 7138000 | 7418000 | 7941000 | 7710000 | 8315000 | 9763000 | 9935000 | 8568000 | 8426000 | 7080000 | 8267000 | 9107000 | 8322000 | 8131000 | 8799000 | 8908000 | 10379000 | 8193000 | 10331000 | 10003000 | 7873000 | 6095000 | 7224000 | 7120000 | 8696000 | 9018000 | 11490000 | 12237000 | 12647000 | 9180000 | 8303000 | 7964000 | 6997000 | 7267000 | 6151000 | 6702000 | 6812000 | 8085000 | 10164000 | 9666000 | 11447000 | 10941000 | 10291000 | 9570000 | 7613000 | 8007000 | 8367000 | 7171000 | 6867000 | 6765000 | 8408000 | 11258000 | 9948000 | 9881000 | 9699000 | 11874000 | 6197000 | 6929000 | 9185000 | 6669000 | 6410000 | 7243000 | 8454000 | 10408000 | 10627000 | 11426000 | 10160000 | 9786000 | 7235000 | 6489000 | 7248000 | 6897000 | 6939000 | 7924000 | 7931000 | 7981000 | 11294000 | 9300000 | 8365000 | 7905000 | 7705000 | 6552000 | 6920000 | 6471000 | 7293000 | 6715000 | 7018000 | 8431000 | 10760000 | 13825000 | 10725000 | 10727000 | 10156000 | 8200000 | 7891000 | 7071000 | 7198000 | 7385000 | 8211190 | 12582800 | 8133170 | 11105400 | 8250000 | 7383000 | 6639000 | 7400000 | 7250000 | 6437000 | 6033000 | 5901000 | 7273000 | 8004000 | 10459000 | 7876000 | 7642000 | 8467000 | 6642000 | 6072000 | 6304000 | 7289000 | 6255000 | 5781000 | 7003000 | 11074000 | 10234000 | 9343000 | 8742000 | 7068000 | 7804000
| 7697000 | 8126000 | 14711000 | 11759000 | 9074000 | 9893000 | 9368000 | 7860000 | 8132000 | 7426000 | 7634000 | 7662000 | 7778000 | 9782000 | 8379000 | 9706000 | 8900000 | 9123000 | 8127000 | 8170000 | 7281000 | 7935000 | 7270000 | 7361000 | 8196000 | 8336000 | 8312000 | 9404000 | 11948000 | 9538000 | 8160000 | 8090000 | 6733000 | 6534000 | 7333000 | 6460000 | 7686000 | 9119000 | 8650000 | 9855000 | 9384000 | 7183000 | 6798000 | 7645000 | 6294000 | 7621000 | 5141000 | 5181000 | 7998000 | 6968000 | 5323000 | 9174000 | 6133000 | 7702000 | 7592000 | 6392000 | 8597000 | 7281000 | 6698949 | 6838000 | 6436000 | 9009000 | 9499000 | 8370000 | 10917000 | 7957000 | 7639000 | 7598000 | 7581000 | 9373000 | 7438000 | 8099000 | 7654000 | 10050000 | 10204000 | 9906000 | 9524000 | 10713000 | 8451000 | 10300000 | 7700000 | 7688000 | 5487000 | 9456000 | 9912000 | 12807000 | 12921000 | 10470000 | 10623000 | 7873000 | 7293000 | 7381000 | 6512000 | 6808000 | 6922000 | 6940000 | 7181000 | 9571000 | 9912000 | 10611000 | 10554000 | 9954000 | 8776000 | 7729000 | 6664000 | 7174000 | 6878000 | 7915000 | 6744000 | 8106000 | 10308000 | 8736000 | 10723000 | 10195000 | 8937000 | 7196000 | 6798000 | 9757000 | 7332000 | 7166000 | 6235000 | 7943000 | 9849000 | 11318000 | 12449000 | 9268000 | 7538000 | 7758000 | 7408000 | 6772000 | 7607000 | 7429000 | 6679000 | 7966000 | 8650000 | 7901000 | 9833000 | 8540000 | 7652000 | 6763000 | 7756000 | 6283000 | 7125000 | 6672000 | 7196000 | 7216000 | 11289000 | 9764000 | 14120000 | 10023000 | 9407000 | 8374000 | 8157000 | 7702000 | 8668000 | 7458000 | 7393000 | 8059300 | 11172630 | 9305130 | 11539490 | 7166000 | 8138000 | 7758000 | 8274000 | 6503000 | 6451000 | 6602000 | 6357000 | 8122000 | 9092000 | 11066000 | 10468000 | 10186000 | 8507000 | 5852000 | 4981000 | 5785000 | 6052000 | 4735000 | 5250000 | 7538000 | 8022000 | 12035000 | 9430000 | 5294000 | 7325000 | 6779000
| 8195000 | 8153000 | 14524000 | 13586000 | 9254000 | 8687000 | 8287000 | 8382000 | 7508000 | 7555000 | 7897000 | 7348000 | 8257000 | 9419000 | 8786000 | 8956000 | 10043000 | 8007000 | 7545000 | 7991000 | 7593000 | 8180000 | 7503000 | 6892000 | 8238000 | 8048000 | 8156000 | 10318000 | 12410000 | 9559000 | 10253000 | 7713000 | 7708000 | 7490000 | 7475000 | 7450000 | 7529000 | 9438000 | 7653000 | 9032000 | 9730000 | 8620000 | 5830000 | 7427000 | 6294000 | 7013000 | 7301000 | 7979000 | 4643000 | 8910000 | 5364000 | 11897000 | 7735000 | 7931000 | 6305000 | 7728000 | 6489000 | 6403000 | 6867387 | 6742000 | 7186000 | 9048000 | 6247000 | 9709000 | 10496000 | 7880000 | 8295000 | 7446000 | 6754000 | 7683000 | 8534000 | 7714000 | 6748000 | 9090000 | 7771000 | 8381000 | 8786000 | 9787000 | 7614000 | 4705000 | 7284000 | 7063000 | 7427000 | 6799000 | 9303000 | 11992000 | 12971000 | 10095000 | 11490000 | 6765000 | 7933000 | 7266000 | 7012000 | 6881000 | 7073000 | 7589000 | 7686000 | 7867000 | 11803000 | 10763000 | 11066000 | 9910000 | 9331000 | 7244000 | 7686000 | 6843000 | 6880000 | 6490000 | 7040000 | 8093000 | 11779000 | 7956000 | 8960000 | 10016000 | 8859000 | 6746000 | 7023000 | 8951000 | 7434000 | 6361000 | 7472000 | 7943000 | 10096000 | 11502000 | 8509000 | 9173000 | 8087000 | 8213000 | 7347000 | 7436000 | 7436000 | 6808000 | 6991000 | 6667000 | 8052000 | 10392000 | 10930000 | 9043000 | 7568000 | 6615000 | 6183000 | 6752000 | 6350000 | 6694000 | 6868000 | 7319000 | 8988000 | 9601000 | 12347000 | 9616000 | 9942000 | 9244000 | 8280000 | 8403000 | 7552000 | 7154000 | 8558000 | 8035230 | 8711680 | 8636980 | 9660000 | 8689000 | 7306000 | 7739000 | 7286000 | 8597000 | 5955000 | 8576000 | 6715000 | 8096000 | 9283000 | 9376000 | 9654000 | 7821000 | 6549000 | 5880000 | 6294000 | 7622000 | 5645000 | 6966000 | 7159000 | 8482000 | 9705000 | 10881000 | 9630000 | 5806000 | 7400000 | 7667000
| 8719000 | 9372000 | 14306000 | 11716000 | 9279000 | 8908000 | 8672000 | 8330000 | 6421000 | 7825000 | 7880000 | 7523000 | 8345000 | 8037000 | 8410000 | 10430000 | 10339000 | 11453000 | 7996000 | 7606000 | 7011000 | 7467000 | 7455000 | 8118000 | 7674000 | 8160000 | 7445000 | 11447000 | 11002000 | 9217000 | 8008000 | 6846000 | 7053000 | 6807000 | 7263000 | 6234000 | 7317000 | 8610000 | 8410000 | 11706000 | 8582000 | 7570000 | 6492000 | 6408000 | 6294000 | 6034000 | 4505000 | 4397000 | 5413000 | 5409000 | 5497000 | 10412000 | 8246000 | 6993000 | 7188000 | 6753000 | 6132000 | 7073000 | 6760502 | 6935000 | 6705000 | 7964000 | 6451000 | 11300000 | 10328000 | 8296000 | 7606000 | 7240000 | 7138000 | 7844000 | 7870000 | 7306000 | 7858000 | 11062000 | 9162000 | 9302000 | 10137000 | 8936000 | 8214000 | 7311000 | 7074000 | 7070000 | 8171000 | 8163000 | 9278000 | 10045000 | 12705000 | 11556000 | 11697000 | 8589000 | 8809000 | 7123000 | 6861000 | 7051000 | 6400000 | 7268000 | 7660000 | 10106000 | 11023000 | 11710000 | 8850000 | 10335000 | 8001000 | 8049000 | 7686000 | 7488000 | 7232000 | 7504000 | 6752000 | 7632000 | 9223000 | 8448000 | 9676000 | 9509000 | 8336000 | 7825000 | 6877000 | 7747000 | 6897000 | 6675000 | 6714000 | 7943000 | 8886000 | 11161000 | 8881000 | 8619000 | 7912000 | 6913000 | 6693000 | 6981000 | 6805000 | 7534000 | 6556000 | 8335000 | 8026000 | 10965000 | 10833000 | 7199000 | 6089000 | 7119000 | 7219000 | 6877000 | 6989000 | 6457000 | 7612000 | 6999000 | 8581000 | 11166000 | 12592000 | 11501000 | 9325000 | 9806000 | 7770000 | 8844000 | 7362000 | 7173000 | 7395000 | 9016290 | 9549980 | 10093630 | 8521000 | 9099000 | 8115000 | 7635000 | 7850000 | 9043000 | 6695000 | 6836000 | 6696000 | 7686000 | 8630000 | 8005000 | 10252000 | 7863000 | 8010000 | 6724000 | 5728000 | 5392000 | 7032000 | 6581000 | 6534000 | 8252000 | 9922000 | 7283000 | 9157000 | 8562000 | 7840000 | 7243000
| 8704000 | 8977000 | 13335000 | 12806000 | 9222000 | 7538000 | 7981000 | 8601000 | 8239000 | 8110000 | 7528000 | 7278000 | 7685000 | 8427000 | 9105000 | 8997000 | 10710000 | 8703000 | 8042000 | 7365000 | 7765000 | 8437000 | 6962000 | 7055000 | 7200000 | 8592000 | 8423000 | 12813000 | 10300000 | 8216000 | 7683000 | 7623000 | 7532000 | 7401000 | 7803000 | 7200000 | 7596000 | 8528000 | 7605000 | 9803000 | 8293000 | 7109000 | 6146000 | 6848000 | 6294000 | 6246000 | 6384000 | 4640000 | 5340000 | 5267000 | 7556000 | 8083000 | 8596000 | 7756000 | 7678000 | 6606000 | 4966000 | 7085000 | 7442442 | 6905000 | 7328000 | 9909000 | 6979000 | 12131000 | 7661000 | 8493000 | 8151000 | 6734000 | 7645000 | 8503000 | 7801000 | 8041000 | 10032000 | 7675000 | 9588000 | 10046000 | 8775000 | 10723000 | 8193000 | 6908000 | 7136000 | 8553000 | 7710000 | 7986000 | 8725000 | 10302000 | 10885000 | 11705000 | 10476000 | 8798000 | 8695000 | 7062000 | 7198000 | 7481000 | 7835000 | 6855000 | 8190000 | 8183000 | 10837000 | 11364000 | 11486000 | 10407000 | 10156000 | 7560000 | 7337000 | 7632000 | 7513000 | 7094000 | 6993000 | 6924000 | 9602000 | 9133000 | 10867000 | 10343000 | 9152000 | 6729000 | 7301000 | 6219000 | 6752000 | 7286000 | 6964000 | 7943000 | 11498000 | 10254000 | 9524000 | 8917000 | 8630000 | 6815000 | 6708000 | 6798000 | 7922000 | 8220000 | 7464000 | 8866000 | 8630000 | 11145000 | 9876000 | 9072000 | 7147000 | 6742000 | 6217000 | 6972000 | 6436000 | 13324000 | 6708000 | 7611000 | 11146000 | 10440000 | 11853000 | 10950000 | 10128000 | 10682000 | 8261000 | 7920000 | 6951000 | 7185000 | 7856000 | 8786380 | 9618040 | 12076500 | 10467000 | 8710000 | 6580000 | 7233000 | 6746000 | 6309000 | 5583000 | 6110000 | 6537000 | 9373000 | 8319000 | 10647000 | 9582000 | 7686000 | 6144000 | 6418000 | 6820000 | 6079000 | 7855000 | 6027000 | 6244000 | 7640000 | 10070000 | 10617000 | 9238000 | 10300000 | 7254000 | 7446000
| 7568000 | 10324000 | 10501000 | 12841000 | 10090000 | 8542000 | 8443000 | 7410000 | 7742000 | 7976000 | 7453000 | 7855000 | 8085000 | 8505000 | 8710000 | 9320000 | 11906000 | 8800000 | 7251000 | 6915000 | 7513000 | 7809000 | 8207000 | 7656000 | 7270000 | 9605000 | 9199000 | 11382000 | 10493000 | 7963000 | 8083000 | 7747000 | 6922000 | 6613000 | 6977000 | 7366000 | 6995000 | 8636000 | 8838000 | 12314000 | 7915000 | 7084000 | 7285000 | 7463000 | 6294000 | 5858000 | 6602000 | 5515000 | 7327000 | 8385000 | 10485000 | 11829000 | 7558000 | 7953000 | 7235000 | 6191000 | 6069000 | 6086000 | 6346666 | 7221000 | 6348000 | 8280000 | 8746000 | 11934000 | 10202000 | 8314000 | 8538000 | 8690000 | 7455000 | 7472000 | 7593000 | 8126000 | 8659000 | 8125000 | 11343000 | 9724000 | 10640000 | 9691000 | 10099000 | 7104000 | 7380000 | 8124000 | 7290000 | 8222000 | 9358000 | 13239000 | 9838000 | 11287000 | 11405000 | 10082000 | 8458000 | 7268000 | 7206000 | 7077000 | 7902000 | 7241000 | 10250000 | 9975000 | 11835000 | 10747000 | 9522000 | 9463000 | 9779000 | 7946000 | 7231000 | 8131000 | 7232000 | 6028000 | 8081000 | 8116000 | 8563000 | 9849000 | 9200000 | 11288000 | 8944000 | 6476000 | 8489000 | 8008000 | 6586000 | 6648000 | 6525000 | 7943000 | 11351000 | 11880000 | 9686000 | 10195000 | 8489000 | 7073000 | 6839000 | 7773000 | 7029000 | 6588000 | 6454000 | 9450000 | 7813000 | 11059000 | 10831000 | 8910000 | 7076000 | 7409000 | 7269000 | 6721000 | 6958000 | 9207000 | 6423000 | 7995000 | 10744000 | 9252000 | 10415000 | 10867000 | 9941000 | 9913000 | 8212000 | 8203000 | 7712000 | 6982000 | 6973000 | 8606270 | 8469320 | 10048810 | 9751000 | 8907000 | 7129000 | 7411000 | 7617000 | 7082000 | 7043000 | 5912000 | 5937000 | 7371000 | 9073000 | 9837000 | 10607000 | 6846000 | 5628000 | 5626000 | 6090000 | 6805000 | 6346000 | 5029000 | 6286000 | 8020000 | 9784000 | 9158000 | 10497000 | 10631000 | 7736000 | 7386000
| 8207000 | 11166000 | 9532000 | 13700000 | 9773000 | 9285000 | 8898000 | 8628000 | 7396000 | 8632000 | 7945000 | 8004000 | 7692000 | 9348000 | 9085000 | 9939000 | 13514000 | 9162000 | 8543000 | 8159000 | 7771000 | 7567000 | 7145000 | 7674000 | 8135000 | 10222000 | 9031000 | 10467000 | 11148000 | 7965000 | 7928000 | 8491000 | 6870000 | 7341000 | 7394000 | 7126000 | 6603000 | 8975000 | 10201000 | 10097000 | 8346000 | 8617000 | 6832000 | 6411000 | 6294000 | 5726000 | 5675000 | 8007000 | 9222000 | 7197000 | 6320000 | 9943000 | 10353000 | 6909000 | 7594000 | 7102000 | 6090000 | 6567000 | 6686158 | 5699000 | 7738000 | 10324000 | 8505000 | 12068000 | 5321000 | 9422000 | 7328000 | 7602000 | 7916000 | 6744000 | 8528000 | 7960000 | 7383000 | 9099000 | 11364000 | 9993000 | 10747000 | 11188000 | 9524000 | 7245000 | 7125000 | 7883000 | 8543000 | 7367000 | 9988000 | 13188000 | 11122000 | 10962000 | 11823000 | 9890000 | 8377000 | 7081000 | 6800000 | 6551000 | 9940000 | 7207000 | 8577000 | 10376000 | 10455000 | 11778000 | 10873000 | 10437000 | 8734000 | 7789000 | 8095000 | 6679000 | 6888000 | 6754000 | 7161000 | 8085000 | 7937000 | 10257000 | 10290000 | 10532000 | 9310000 | 6895000 | 6516000 | 9122000 | 7254000 | 6255000 | 7708000 | 7943000 | 10540000 | 10400000 | 11196000 | 8450000 | 8640000 | 7794000 | 7664000 | 6795000 | 7018000 | 6352000 | 7545000 | 8209000 | 8274000 | 10613000 | 10643000 | 8247000 | 9112000 | 7684000 | 6552000 | 5755000 | 5940000 | 7218000 | 6135000 | 7906000 | 10393000 | 12225000 | 10055000 | 10353000 | 10977000 | 9083000 | 7883000 | 6469000 | 7007000 | 6998000 | 7471000 | 9798150 | 9422160 | 7964680 | 10151000 | 7307000 | 7453000 | 7410000 | 7370000 | 6980000 | 5713000 | 7169000 | 6101000 | 8679000 | 10048000 | 9517000 | 11127000 | 8376000 | 6786000 | 6088000 | 6053000 | 6850000 | 5369000 | 4436000 | 6387000 | 9014000 | 9278000 | 8576000 | 9823000 | 8935000 | 7322000 | 8024000
| 8267000 | 8519000 | 8867000 | 15467000 | 9994000 | 9469000 | 8866000 | 7965000 | 7096000 | 9281000 | 8000000 | 8235000 | 7871000 | 9561000 | 8858000 | 8136000 | 13722000 | 8661000 | 7440000 | 7974000 | 7152000 | 7595000 | 7331000 | 7889000 | 8412000 | 8236000 | 9863000 | 10526000 | 11235000 | 9434000 | 7958000 | 6680000 | 7181000 | 6691000 | 7846000 | 6427000 | 7763000 | 7726000 | 8476000 | 11074000 | 8373000 | 6799000 | 6771000 | 7462000 | 6294000 | 7793000 | 5698000 | 8492000 | 5090000 | 5259000 | 7965000 | 6530000 | 7561000 | 7202000 | 7049000 | 7331000 | 6398000 | 8005000 | 7558024 | 6764000 | 6123000 | 8047000 | 7694000 | 14718000 | 10250000 | 8672000 | 8086000 | 7534000 | 6868000 | 7873000 | 7713000 | 8453000 | 6950000 | 9295000 | 10366000 | 11443000 | 10353000 | 10594000 | 10024000 | 6858000 | 6882000 | 5989000 | 7636000 | 8011000 | 8082000 | 12803000 | 10751000 | 12126000 | 10979000 | 9644000 | 8073000 | 7657000 | 7345000 | 7379000 | 8090000 | 7114000 | 8647000 | 9577000 | 11922000 | 11983000 | 11180000 | 10260000 | 10131000 | 6608000 | 7591000 | 7686000 | 7103000 | 6884000 | 7305000 | 9415000 | 8320000 | 8781000 | 9817000 | 9618000 | 8958000 | 7314000 | 6283000 | 8228000 | 6600000 | 6830000 | 8764000 | 7943000 | 10648000 | 9243000 | 10602000 | 10708000 | 8471000 | 6942000 | 6649000 | 6794000 | 7488000 | 6434000 | 8260000 | 9048000 | 8582000 | 8691000 | 9814000 | 8670000 | 8474000 | 6569000 | 6728000 | 7369000 | 5787000 | 7351000 | 6612000 | 6995000 | 11281000 | 11910000 | 10572000 | 10146000 | 9558000 | 9068000 | 7460000 | 7281000 | 7721000 | 7645000 | 7533000 | 9793170 | 9520930 | 9082690 | 10089000 | 7301000 | 7318000 | 7504000 | 7590000 | 7861000 | 6197000 | 6972000 | 6781000 | 8132000 | 9412000 | 9535000 | 9387000 | 8302000 | 5970000 | 6175000 | 6231000 | 6799000 | 6091000 | 4853000 | 5546000 | 7529000 | 10914000 | 8099000 | 9685000 | 8307000 | 7903000 | 7447000
| 8832000 | 7657000 | 10445000 | 15202000 | 8218000 | 9790000 | 8447000 | 6958000 | 7398000 | 9506000 | 7249000 | 7262000 | 8250000 | 11025000 | 8228000 | 8607000 | 12087000 | 9826000 | 8031000 | 7897000 | 7632000 | 7979000 | 7600000 | 7787000 | 7980000 | 9294000 | 10638000 | 10537000 | 11694000 | 8462000 | 8177000 | 7108000 | 6980000 | 7043000 | 7751000 | 7265000 | 7735000 | 9119000 | 9109000 | 12001000 | 9662000 | 6424000 | 6101000 | 5883000 | 6294000 | 5519000 | 5598000 | 5060000 | 6680000 | 7532000 | 10009000 | 9312000 | 7077000 | 7782000 | 7501000 | 6606000 | 6591000 | 5562000 | 7027204 | 7551000 | 6625000 | 9800000 | 9026000 | 10585000 | 9413000 | 8284000 | 7837000 | 7557000 | 8150000 | 8375000 | 9070000 | 7759000 | 7214000 | 9386000 | 10801000 | 11836000 | 10546000 | 10366000 | 7868000 | 6600000 | 7093000 | 7476000 | 7045000 | 7770000 | 7704000 | 11378000 | 12333000 | 13260000 | 11129000 | 11890000 | 7558000 | 8327000 | 6458000 | 7167000 | 8175000 | 6977000 | 8948000 | 9468000 | 9671000 | 12592000 | 10732000 | 10701000 | 8959000 | 6967000 | 7413000 | 7474000 | 7359000 | 7233000 | 7961000 | 10059000 | 9897000 | 10935000 | 9695000 | 8088000 | 9585000 | 7072000 | 7584000 | 7749000 | 6566000 | 6560000 | 6790000 | 7943000 | 11069000 | 10080000 | 11236000 | 8766000 | 9009000 | 6441000 | 7773000 | 7555000 | 7666000 | 7609000 | 8388000 | 7717000 | 8191000 | 9460000 | 9753000 | 8668000 | 7026000 | 6572000 | 6373000 | 7069000 | 7355000 | 6067000 | 5879000 | 8293000 | 11637000 | 11953000 | 10722000 | 10502000 | 9565000 | 8496000 | 7287000 | 8354000 | 7469000 | 7219000 | 7247000 | 10023910 | 11458150 | 11620830 | 8623000 | 7384000 | 7265000 | 7875000 | 7194000 | 7586000 | 6401000 | 6273000 | 6801000 | 8396000 | 8413000 | 8924000 | 9985000 | 8042000 | 7492000 | 6074000 | 6452000 | 6366000 | 5561000 | 4640000 | 7141000 | 8692000 | 8122000 | 7596000 | 7837000 | 7937000 | 8208000 | 7187000
| 8878000 | 8918000 | 9751000 | 15874000 | 9438000 | 9012000 | 8359000 | 8905000 | 7186000 | 9156000 | 8215000 | 7689000 | 7821000 | 11826000 | 8232000 | 8696000 | 11387000 | 9081000 | 9046000 | 7763000 | 7304000 | 7346000 | 7323000 | 7280000 | 8008000 | 9432000 | 10801000 | 10361000 | 11215000 | 10036000 | 7672000 | 7598000 | 8153000 | 7434000 | 7045000 | 6434000 | 6978000 | 8102000 | 9491000 | 11392000 | 9730000 | 7307000 | 6537000 | 6978000 | 6294000 | 6703000 | 6354000 | 5644000 | 9320000 | 9205000 | 9521000 | 8508000 | 7548000 | 6748000 | 6466000 | 6840000 | 5976000 | 8431000 | 5932782 | 6280000 | 6924000 | 10167000 | 9061000 | 9554000 | 10516000 | 9018000 | 7664000 | 7915000 | 6803000 | 7239000 | 7807000 | 7905000 | 6922000 | 9647000 | 11521000 | 11454000 | 8547000 | 9134000 | 6705000 | 7634000 | 7029000 | 6830000 | 9109000 | 8294000 | 8450000 | 13814000 | 11964000 | 12545000 | 10975000 | 7719000 | 6728000 | 8323000 | 7079000 | 7066000 | 6294000 | 7383000 | 8377000 | 8562000 | 11268000 | 11756000 | 11338000 | 8897000 | 8909000 | 8009000 | 7190000 | 7151000 | 7190000 | 7151000 | 8098000 | 9728000 | 10251000 | 11079000 | 10150000 | 8907000 | 8567000 | 6769000 | 6939000 | 8662000 | 7037000 | 7644000 | 6994000 | 7943000 | 11126000 | 11417000 | 10046000 | 7838000 | 8247000 | 7473000 | 6531000 | 8006000 | 6842000 | 6714000 | 7576000 | 8345000 | 7846000 | 11696000 | 9502000 | 8602000 | 6544000 | 6188000 | 6956000 | 6271000 | 6566000 | 7176000 | 6582000 | 10646000 | 12233000 | 11458000 | 11435000 | 9730000 | 8137000 | 8783000 | 7228000 | 7642000 | 6848000 | 7380000 | 7428000 | 9935100 | 10614040 | 10976750 | 8189000 | 7822000 | 7691000 | 7613000 | 7511000 | 6932000 | 6470000 | 6550000 | 7043000 | 7690000 | 9314000 | 11137000 | 10485000 | 9286000 | 5746000 | 5698000 | 6518000 | 6336000 | 6012000 | 6355000 | 4930000 | 7563000 | 7698000 | 9537000 | 6659000 | 7922000 | 7332000 | 7506000
| 9167000 | 9605000 | 11288000 | 14161000 | 9886000 | 8983000 | 8213000 | 8739000 | 7370000 | 8161000 | 7639000 | 8341000 | 7710000 | 10365000 | 7804000 | 8329000 | 12341000 | 8195000 | 7727000 | 7974000 | 7203000 | 7439000 | 8291000 | 7839000 | 8140000 | 8520000 | 9374000 | 9585000 | 9279000 | 9532000 | 7736000 | 6494000 | 6695000 | 6762000 | 7179000 | 7750000 | 7276000 | 8132000 | 9143000 | 13477000 | 9341000 | 6430000 | 5801000 | 6370000 | 6294000 | 5832000 | 4842000 | 7984000 | 4627000 | 5555000 | 10580000 | 8526000 | 7407000 | 6831000 | 7379000 | 6594000 | 6189000 | 6933000 | 7380058 | 6079000 | 6332000 | 8169000 | 10909000 | 12014000 | 11128000 | 8174000 | 8202000 | 7554000 | 7643000 | 7810000 | 7305000 | 7208000 | 6787000 | 10028000 | 8759000 | 11176000 | 8513000 | 10441000 | 8018000 | 7476000 | 7316000 | 6678000 | 8834000 | 8231000 | 8405000 | 12104000 | 8736000 | 12022000 | 9630000 | 9176000 | 8344000 | 7897000 | 6955000 | 6681000 | 6414000 | 8060000 | 6800000 | 9491000 | 10953000 | 12290000 | 9530000 | 9643000 | 7977000 | 6893000 | 7975000 | 8233000 | 7214000 | 7128000 | 7887000 | 10045000 | 10508000 | 10845000 | 11295000 | 9610000 | 8501000 | 6909000 | 7001000 | 7591000 | 6865000 | 6320000 | 7465000 | 7943000 | 11691000 | 10532000 | 9674000 | 9080000 | 7796000 | 6731000 | 8429000 | 6716000 | 6421000 | 7096000 | 7859000 | 9732000 | 7882000 | 10641000 | 9378000 | 9087000 | 6594000 | 6949000 | 5822000 | 6231000 | 7103000 | 7216000 | 6872000 | 6350000 | 12310000 | 10967000 | 12257000 | 10096000 | 8848000 | 8791000 | 8588000 | 7763000 | 7314000 | 6645000 | 7783000 | 10169160 | 10345120 | 11053110 | 8407000 | 8130000 | 7691000 | 6848000 | 6651000 | 5072000 | 6713000 | 5910000 | 7797000 | 8189000 | 6942000 | 11106000 | 10920000 | 8642000 | 6858000 | 5573000 | 6215000 | 6194000 | 5553000 | 5442000 | 7790000 | 7336000 | 9984000 | 10227000 | 7436000 | 8033000 | 7220000 | 6414000
| 9323000 | 9784000 | 10761000 | 12876000 | 10245000 | 8616000 | 8330000 | 8265000 | 6719000 | 7941000 | 6911000 | 7359000 | 7484000 | 9364000 | 8211000 | 8539000 | 9866000 | 9461000 | 7865000 | 6943000 | 7726000 | 7970000 | 7013000 | 7527000 | 8667000 | 9721000 | 8912000 | 10032000 | 8301000 | 9160000 | 7781000 | 7264000 | 7048000 | 7200000 | 7019000 | 6513000 | 6183000 | 8281000 | 10063000 | 12427000 | 8747000 | 6200000 | 6341000 | 6500000 | 6294000 | 5318000 | 6850000 | 5392000 | 6055000 | 7763000 | 6889000 | 8793000 | 7621000 | 6954000 | 6978000 | 6889000 | 6235000 | 6454000 | 6707429 | 7155000 | 7818000 | 8041000 | 10259000 | 7912000 | 9361000 | 8690000 | 7953000 | 8834000 | 8151000 | 7827000 | 7295000 | 8086000 | 7025000 | 9066000 | 11388000 | 10040000 | 10274000 | 10845000 | 8953000 | 6684000 | 8807000 | 7095000 | 7289000 | 7816000 | 7492000 | 11107000 | 10960000 | 12705000 | 9204000 | 9381000 | 9093000 | 7330000 | 6866000 | 7124000 | 7398000 | 6468000 | 8610000 | 10746000 | 12325000 | 12917000 | 10279000 | 9951000 | 8033000 | 7386000 | 7015000 | 9250000 | 7166000 | 7412000 | 7397000 | 8380000 | 8426000 | 10570000 | 10713000 | 8182000 | 7906000 | 7304000 | 7533000 | 6645000 | 6250000 | 6457000 | 7914000 | 7943000 | 9952000 | 7794000 | 10687000 | 8827000 | 9088000 | 6946000 | 7350000 | 7605000 | 7815000 | 7269000 | 7179000 | 9914000 | 8869000 | 10382000 | 9803000 | 8646000 | 8459000 | 6638000 | 7191000 | 6405000 | 5950000 | 7674000 | 7144000 | 9544000 | 13042000 | 10903000 | 12736000 | 9996000 | 9388000 | 7552000 | 7607000 | 9070000 | 6533000 | 6498000 | 7710000 | 10221450 | 11004140 | 9974110 | 8629000 | 8960000 | 7191000 | 7930000 | 7592000 | 6082000 | 5446000 | 6707000 | 7665000 | 7822000 | 9176000 | 12199000 | 8893000 | 6879000 | 6480000 | 7695000 | 6630000 | 7795000 | 6845000 | 5883000 | 5845000 | 6287000 | 8098000 | 10866000 | 7495000 | 8907000 | 6988000 | 7589000
| 9634000 | 9377000 | 10507000 | 13742000 | 9956000 | 9789000 | 8628000 | 7927000 | 6969000 | 7961000 | 7408000 | 7830000 | 8803000 | 8792000 | 8225000 | 8164000 | 10423000 | 9444000 | 7024000 | 7973000 | 7965000 | 7764000 | 8291000 | 6959000 | 7835000 | 11465000 | 11486000 | 10790000 | 8050000 | 10073000 | 7851000 | 7617000 | 6984000 | 7084000 | 6740000 | 6638000 | 6575000 | 9137000 | 8645000 | 10354000 | 8704000 | 6638000 | 7011000 | 6909000 | 6294000 | 6214000 | 5332000 | 4776000 | 7315000 | 7981000 | 9910000 | 8319000 | 9982000 | 6962000 | 7978000 | 6727000 | 6906000 | 6827000 | 6854428 | 6292000 | 6476000 | 8583000 | 10950000 | 9829000 | 10243000 | 7660000 | 8582000 | 8131000 | 8116000 | 7613000 | 8555000 | 7943000 | 7575000 | 7899000 | 11990000 | 11608000 | 11112000 | 10776000 | 8974000 | 7626000 | 8559000 | 7267000 | 8113000 | 8112000 | 7707000 | 13566000 | 11242000 | 10384000 | 10289000 | 10032000 | 8913000 | 7111000 | 6709000 | 7098000 | 7534000 | 7543000 | 8427000 | 10327000 | 12118000 | 12686000 | 9696000 | 9366000 | 8303000 | 7558000 | 8388000 | 8289000 | 6739000 | 7159000 | 7654000 | 8867000 | 8929000 | 8413000 | 11370000 | 7962000 | 9008000 | 6860000 | 6917000 | 6867000 | 7025000 | 7360000 | 7166000 | 7943000 | 9901000 | 9085000 | 10861000 | 9113000 | 8457000 | 7800000 | 7624000 | 7128000 | 7409000 | 8175000 | 6884000 | 9496000 | 9224000 | 8275000 | 9266000 | 8636000 | 8046000 | 7112000 | 7083000 | 6972000 | 6407000 | 6267000 | 6790000 | 7409000 | 12752000 | 12277000 | 11528000 | 10678000 | 10499000 | 7226000 | 7950000 | 8549000 | 6543000 | 7608000 | 6865000 | 10960150 | 9844630 | 10132640 | 7254000 | 6521000 | 6302000 | 7739000 | 6038000 | 5672000 | 5262000 | 6651000 | 6678000 | 9491000 | 9734000 | 11067000 | 9492000 | 7751000 | 5942000 | 7728000 | 5884000 | 7051000 | 5968000 | 5658000 | 5982000 | 6760000 | 9389000 | 10564000 | 7487000 | 7867000 | 7716000 | 7308000
| 9604000 | 9292000 | 11783000 | 13302000 | 9819000 | 9422000 | 8743000 | 8451000 | 7549000 | 8294000 | 8158000 | 7591000 | 9129000 | 9470000 | 8546000 | 9268000 | 13193000 | 9315000 | 9026000 | 7916000 | 7525000 | 7464000 | 7048000 | 7978000 | 7940000 | 10976000 | 9627000 | 10694000 | 8698000 | 8719000 | 8264000 | 6649000 | 6888000 | 6921000 | 7218000 | 7215000 | 7730000 | 8366000 | 7680000 | 10068000 | 8889000 | 6939000 | 6486000 | 6997000 | 6294000 | 6959000 | 5875000 | 7899000 | 4943000 | 5253000 | 7661000 | 9100000 | 11380000 | 6929000 | 7926000 | 6891000 | 6665000 | 7783000 | 7217132 | 6659000 | 7980000 | 6477000 | 10142000 | 8103000 | 7605000 | 9108000 | 8909000 | 6923000 | 7970000 | 8216000 | 8344000 | 8196000 | 7803000 | 10274000 | 11472000 | 8287000 | 10535000 | 10548000 | 10207000 | 7898000 | 7756000 | 8020000 | 8432000 | 7557000 | 7731000 | 15385000 | 11706000 | 9143000 | 11223000 | 8909000 | 8214000 | 7736000 | 7072000 | 6758000 | 7407000 | 6849000 | 9724000 | 11701000 | 11736000 | 13089000 | 10843000 | 10634000 | 8096000 | 8174000 | 7145000 | 8856000 | 7279000 | 7170000 | 8059000 | 8873000 | 9234000 | 9385000 | 10806000 | 10288000 | 8906000 | 7368000 | 7777000 | 8153000 | 6847000 | 6866000 | 7471000 | 7943000 | 10094000 | 9952000 | 10056000 | 8499000 | 7682000 | 7150000 | 7187000 | 8039000 | 7399000 | 6000000 | 8037000 | 10152000 | 9901000 | 8908000 | 10051000 | 8043000 | 7900000 | 6066000 | 6985000 | 8077000 | 5878000 | 7003000 | 7272000 | 9235000 | 12179000 | 12537000 | 11623000 | 9880000 | 9438000 | 6839000 | 7155000 | 7176000 | 8007000 | 7759000 | 7007000 | 12074010 | 9515120 | 9724280 | 8736000 | 8778000 | 6852000 | 7548000 | 7258000 | 6043000 | 5570000 | 8055000 | 6907000 | 9129000 | 9515000 | 11223000 | 7864000 | 7108000 | 6708000 | 6557000 | 6541000 | 6437000 | 6486000 | 4692000 | 6136000 | 7579000 | 9869000 | 12029000 | 8093000 | 7826000 | 6729000 | 8464000
| 9793000 | 8954000 | 8858000 | 11487000 | 10704000 | 9574000 | 8740000 | 8140000 | 7103000 | 7518000 | 7679000 | 6799000 | 9451000 | 10208000 | 8637000 | 9979000 | 11567000 | 9087000 | 8976000 | 7762000 | 8338000 | 6628000 | 7830000 | 7441000 | 8003000 | 11906000 | 9428000 | 11973000 | 8517000 | 8807000 | 7308000 | 6919000 | 7566000 | 7624000 | 6942000 | 6740000 | 7827000 | 7668000 | 7407000 | 10583000 | 9467000 | 7038000 | 7020000 | 6248000 | 6294000 | 6028000 | 6334000 | 4809000 | 6588000 | 5907000 | 7363000 | 8993000 | 7729000 | 7019000 | 8050000 | 6994000 | 6345000 | 7249000 | 6321951 | 6375000 | 6713000 | 7532000 | 12339000 | 8225000 | 9660000 | 8481000 | 7930000 | 7595000 | 7108000 | 8109000 | 7932000 | 8279000 | 6922000 | 9186000 | 10246000 | 9802000 | 11735000 | 10978000 | 9218000 | 7429000 | 7239000 | 6868000 | 7924000 | 8035000 | 7768000 | 15520000 | 12042000 | 11519000 | 11001000 | 9859000 | 7524000 | 6175000 | 7377000 | 7441000 | 7111000 | 7408000 | 8847000 | 10779000 | 11782000 | 14435000 | 10993000 | 10851000 | 9778000 | 7277000 | 7198000 | 6780000 | 7308000 | 6724000 | 7609000 | 8764000 | 9397000 | 8130000 | 11248000 | 10715000 | 7486000 | 6631000 | 6067000 | 7239000 | 6757000 | 6259000 | 8487000 | 7943000 | 11612000 | 9257000 | 10229000 | 9566000 | 8568000 | 7055000 | 5974000 | 8540000 | 6647000 | 6598000 | 7986000 | 7212000 | 9395000 | 8648000 | 9801000 | 8133000 | 7459000 | 7276000 | 7782000 | 6658000 | 7252000 | 7567000 | 6773000 | 7738000 | 12769000 | 13663000 | 11211000 | 10835000 | 10112000 | 8996000 | 10699000 | 7948000 | 6845000 | 7773000 | 8487000 | 10811580 | 10274570 | 9986560 | 9186000 | 8006000 | 8736000 | 7867000 | 5930000 | 6366000 | 5524000 | 7311000 | 6696000 | 9269000 | 11156000 | 10921000 | 8932000 | 6594000 | 5516000 | 5999000 | 7159000 | 7565000 | 5596000 | 5048000 | 5871000 | 7327000 | 10508000 | 11195000 | 8190000 | 7958000 | 5969000 | 5479000
| 9707000 | 9752000 | 10094000 | 8888000 | 10953000 | 9453000 | 8553000 | 8884000 | 8359000 | 6955000 | 7927000 | 7865000 | 10103000 | 8950000 | 8773000 | 10290000 | 11221000 | 9251000 | 7580000 | 8044000 | 7360000 | 7668000 | 7195000 | 7450000 | 8486000 | 10741000 | 10580000 | 10780000 | 9451000 | 8039000 | 7740000 | 7580000 | 7230000 | 6579000 | 7671000 | 5968000 | 9139000 | 9001000 | 7030000 | 9595000 | 7336000 | 8740000 | 6478000 | 6684000 | 6294000 | 5968000 | 5564000 | 4823000 | 9544000 | 9187000 | 6537000 | 7815000 | 10298000 | 6880000 | 7373000 | 8677000 | 5258000 | 7839000 | 6726866 | 7117000 | 7647000 | 9600000 | 7602000 | 9211000 | 8963000 | 8310000 | 8116000 | 6028000 | 7357000 | 8151000 | 7677000 | 7514000 | 8254000 | 10328000 | 11403000 | 10342000 | 10584000 | 9380000 | 7308000 | 7026000 | 6172000 | 7085000 | 8625000 | 7709000 | 7722000 | 13981000 | 11757000 | 10800000 | 11707000 | 10471000 | 7081000 | 6814000 | 6565000 | 7054000 | 9333000 | 7708000 | 9275000 | 10975000 | 11297000 | 12641000 | 10996000 | 8906000 | 8174000 | 7876000 | 6740000 | 6515000 | 6960000 | 6632000 | 8933000 | 8700000 | 9479000 | 8459000 | 11255000 | 10070000 | 7512000 | 6829000 | 6342000 | 6841000 | 6476000 | 7217000 | 7886000 | 7943000 | 10676000 | 8582000 | 10480000 | 10128000 | 8915000 | 8178000 | 6080000 | 6653000 | 7717000 | 7095000 | 8026000 | 8315000 | 8799000 | 9201000 | 10986000 | 7688000 | 7655000 | 6328000 | 7010000 | 6180000 | 6658000 | 6965000 | 6812000 | 9766000 | 12131000 | 13016000 | 11505000 | 9531000 | 8483000 | 8364000 | 9811000 | 6995000 | 7369000 | 7606000 | 7335000 | 11730390 | 9415520 | 12148710 | 9934000 | 6852000 | 6510000 | 7452000 | 6443000 | 5902000 | 5843000 | 5853000 | 7049000 | 9620000 | 10124000 | 10544000 | 10078000 | 8271000 | 6311000 | 4972000 | 4577000 | 7607000 | 5690000 | 6048000 | 5907000 | 7723000 | 10197000 | 9976000 | 7670000 | 6893000 | 5818000 | 9055000
| 8809000 | 9218000 | 10624000 | 10020000 | 10422000 | 7743000 | 8256000 | 7744000 | 8102000 | 8063000 | 7372000 | 6515000 | 11861000 | 8821000 | 9013000 | 9514000 | 9813000 | 8745000 | 8450000 | 6504000 | 7924000 | 7897000 | 7467000 | 8143000 | 7986000 | 10770000 | 9647000 | 10272000 | 9946000 | 8206000 | 8035000 | 7287000 | 6780000 | 7515000 | 6409000 | 7224000 | 9445000 | 9759000 | 7873000 | 10384000 | 10445000 | 7283000 | 6056000 | 5914000 | 6294000 | 5888000 | 5319000 | 8193000 | 6236000 | 5726000 | 11099000 | 7618000 | 6379000 | 6694000 | 6289000 | 7132000 | 7339000 | 8351000 | 6757498 | 6711000 | 6906000 | 9900000 | 7439000 | 7141000 | 9267000 | 8494000 | 7578000 | 6148000 | 7413000 | 8545000 | 8011000 | 7699000 | 6984000 | 9039000 | 11423000 | 10671000 | 10981000 | 10824000 | 6382000 | 7332000 | 6058000 | 6737000 | 8274000 | 7527000 | 7739000 | 14610000 | 10817000 | 11999000 | 11221000 | 10977000 | 8005000 | 6876000 | 6898000 | 6910000 | 6747000 | 7386000 | 7090000 | 10950000 | 9979000 | 10803000 | 11103000 | 9653000 | 6801000 | 8957000 | 7292000 | 6387000 | 7137000 | 7255000 | 7781000 | 8666000 | 10820000 | 9757000 | 10898000 | 9848000 | 7390000 | 6212000 | 7699000 | 6729000 | 7138000 | 6765000 | 7202000 | 7943000 | 10025000 | 9740000 | 10752000 | 8185000 | 8528000 | 7008000 | 6406000 | 6532000 | 8510000 | 6383000 | 7900000 | 8636000 | 10017000 | 11544000 | 8101000 | 8095000 | 7040000 | 7584000 | 6221000 | 6449000 | 5875000 | 7098000 | 6342000 | 10167000 | 10038000 | 12020000 | 10893000 | 10890000 | 9499000 | 8119000 | 7512000 | 7195000 | 7087000 | 7250000 | 7408000 | 10028890 | 9153240 | 11046470 | 9895000 | 6946000 | 6209000 | 7585000 | 6660000 | 6047000 | 6312000 | 5586000 | 6287000 | 8572000 | 10994000 | 11032000 | 9597000 | 8657000 | 6109000 | 7483000 | 4474000 | 7148000 | 5517000 | 7310000 | 6128000 | 7298000 | 8712000 | 9914000 | 10270000 | 7742000 | 7098000 | 8584000
| 8793000 | 9978000 | 10440000 | 9663000 | 10305000 | 7299000 | 9264000 | 7537000 | 7686000 | 7905000 | 6766000 | 8320000 | 8568000 | 8660000 | 8318000 | 9036000 | 7437000 | 8254000 | 8382000 | 8613000 | 7256000 | 10249000 | 7517000 | 7504000 | 8123000 | 11042000 | 11111000 | 12079000 | 9974000 | 7930000 | 7219000 | 6539000 | 7040000 | 6504000 | 7616000 | 7327000 | 8942000 | 10182000 | 9064000 | 9466000 | 6696000 | 6088000 | 6306000 | 5572000 | 6294000 | 6003000 | 5772000 | 5082000 | 5037000 | 7095000 | 9890000 | 6665000 | 9628000 | 6053000 | 10791000 | 6492000 | 5781000 | 7723000 | 7290358 | 7067000 | 7258000 | 8439000 | 8908000 | 9472000 | 9789000 | 7759000 | 8337000 | 7256000 | 7423000 | 8495000 | 8078000 | 8962000 | 7384000 | 10744000 | 11892000 | 11052000 | 10814000 | 10939000 | 7906000 | 7806000 | 6495000 | 7271000 | 7555000 | 8175000 | 7414000 | 14122000 | 9514000 | 12044000 | 10909000 | 9150000 | 8632000 | 7817000 | 7082000 | 6747000 | 6463000 | 7307000 | 8040000 | 11485000 | 9707000 | 11078000 | 10646000 | 9895000 | 7625000 | 7360000 | 7543000 | 6784000 | 7519000 | 6720000 | 7098000 | 8103000 | 8674000 | 9303000 | 10917000 | 8477000 | 8064000 | 7269000 | 6804000 | 9357000 | 7199000 | 7068000 | 7568000 | 7943000 | 8833000 | 10180000 | 11521000 | 8489000 | 6799000 | 6910000 | 6958000 | 7245000 | 7543000 | 7305000 | 7896000 | 8620000 | 9272000 | 10737000 | 8704000 | 8826000 | 6091000 | 6838000 | 7336000 | 6187000 | 6684000 | 6610000 | 6712000 | 8257000 | 13194000 | 12132000 | 9540000 | 9752000 | 8490000 | 9105000 | 6839000 | 7516000 | 7053000 | 7391000 | 7178000 | 10736880 | 10109400 | 9412200 | 9231000 | 7263000 | 6606000 | 8384000 | 6391000 | 5979000 | 5513000 | 5645000 | 6811000 | 8996000 | 9475000 | 11153000 | 6881000 | 7483000 | 6134000 | 5587000 | 5047000 | 6108000 | 6168000 | 5750000 | 8034000 | 9010000 | 9331000 | 9648000 | 8564000 | 7925000 | 7466000 | 6003000
| 8591000 | 10889000 | 12224000 | 9556000 | 11440000 | 8635000 | 8319000 | 7548000 | 7444000 | 7782000 | 7486000 | 9031000 | 8606000 | 8798000 | 8578000 | 8469000 | 7993000 | 8863000 | 7886000 | 6930000 | 8346000 | 10377000 | 7999000 | 7440000 | 8088000 | 10253000 | 11923000 | 11857000 | 10903000 | 8337000 | 7254000 | 7386000 | 7684000 | 7670000 | 6574000 | 5848000 | 7323000 | 9797000 | 9699000 | 11329000 | 5804000 | 8041000 | 5916000 | 6237000 | 6294000 | 5337000 | 6285000 | 4519000 | 5397000 | 9342000 | 5239000 | 7923000 | 8058000 | 6759000 | 9079000 | 6625000 | 6555000 | 8515000 | 6231022 | 6928000 | 8667000 | 9810000 | 8798000 | 10975000 | 8672000 | 8961000 | 7756000 | 7846000 | 8219000 | 8199000 | 7776000 | 7240000 | 7734000 | 8715000 | 13136000 | 9516000 | 8599000 | 10548000 | 7160000 | 6500000 | 6658000 | 7060000 | 7362000 | 7138000 | 8061000 | 12381000 | 10425000 | 11418000 | 10316000 | 9901000 | 8811000 | 6645000 | 6313000 | 7345000 | 6758000 | 6450000 | 8066000 | 7738000 | 10717000 | 10261000 | 11202000 | 8679000 | 8602000 | 6794000 | 7191000 | 6800000 | 7464000 | 6953000 | 7395000 | 7259000 | 9560000 | 10099000 | 11190000 | 9202000 | 8455000 | 6980000 | 6598000 | 6546000 | 6277000 | 6150000 | 6566000 | 7943000 | 10992000 | 8965000 | 11298000 | 8173000 | 7727000 | 7459000 | 6585000 | 7354000 | 6069000 | 7829000 | 8201000 | 9180000 | 9330000 | 10217000 | 9316000 | 8460000 | 6499000 | 6498000 | 7360000 | 6559000 | 6559000 | 6763000 | 6786000 | 8203000 | 10889000 | 11366000 | 10051000 | 10699000 | 9694000 | 7888000 | 6929000 | 7500000 | 7176000 | 6204000 | 7330560 | 6928840 | 11883110 | 10594120 | 8208000 | 7527000 | 6838000 | 7026000 | 6881000 | 6465000 | 5245000 | 7891000 | 6419000 | 6897000 | 9289000 | 10549000 | 8050000 | 8804000 | 6019000 | 5132000 | 5309000 | 5946000 | 5432000 | 6338000 | 8744000 | 8297000 | 9695000 | 10643000 | 9350000 | 7939000 | 7272000 | 6933000
| 8380000 | 10287000 | 10376000 | 9417000 | 10042000 | 9521000 | 8358000 | 6995000 | 7269000 | 7796000 | 7703000 | 7618000 | 7781000 | 9977000 | 9538000 | 8152000 | 9622000 | 9955000 | 7645000 | 6893000 | 8358000 | 7761000 | 7471000 | 7884000 | 9029000 | 10825000 | 12893000 | 10539000 | 10982000 | 7732000 | 7580000 | 7062000 | 7145000 | 8130000 | 6611000 | 7329000 | 7396000 | 10505000 | 9266000 | 11397000 | 8109000 | 5151000 | 7031000 | 6267000 | 6294000 | 6056000 | 6309000 | 6190000 | 6629000 | 9507000 | 10888000 | 8418000 | 8352000 | 6217000 | 6850000 | 6383000 | 5750000 | 8372000 | 6901130 | 5962000 | 6918000 | 10857000 | 8489000 | 8796000 | 9591000 | 9450000 | 9422000 | 10230000 | 6947000 | 7381000 | 7699000 | 6180000 | 7608000 | 10272000 | 12485000 | 8435000 | 9929000 | 11476000 | 8482000 | 6698000 | 6302000 | 7554000 | 8496000 | 7975000 | 8890000 | 13536000 | 10152000 | 10021000 | 12133000 | 10498000 | 9064000 | 6753000 | 6985000 | 7003000 | 7323000 | 7422000 | 9240000 | 9488000 | 11493000 | 10861000 | 11666000 | 8170000 | 8878000 | 7688000 | 7761000 | 7436000 | 6825000 | 6682000 | 8190000 | 7746000 | 9264000 | 10973000 | 10077000 | 9396000 | 5612000 | 7953000 | 8008000 | 6716000 | 6696000 | 7532000 | 6847000 | 7943000 | 11414000 | 10579000 | 12358000 | 8249000 | 7068000 | 7324000 | 7596000 | 7344000 | 6249000 | 7388000 | 6921000 | 7910000 | 9229000 | 11695000 | 8872000 | 8126000 | 8101000 | 6769000 | 6560000 | 6842000 | 6994000 | 6019000 | 7192000 | 9423000 | 8837000 | 12615000 | 10390000 | 9411000 | 9485000 | 7867000 | 8095000 | 8265000 | 6930000 | 6700000 | 6696440 | 8008670 | 12440870 | 10276230 | 9026000 | 8014000 | 6827000 | 7665000 | 6935000 | 5731000 | 5617000 | 6676000 | 6705000 | 8681000 | 8397000 | 8858000 | 10093000 | 8628000 | 6351000 | 5659000 | 5853000 | 6750000 | 7049000 | 8541000 | 7493000 | 9138000 | 8514000 | 8941000 | 9628000 | 7616000 | 6601000 | 7679000
| 9850000 | 10131000 | 12649000 | 11406000 | 10507000 | 7997000 | 8974000 | 7538000 | 6765000 | 8076000 | 8278000 | 7547000 | 7549000 | 10203000 | 9048000 | 9097000 | 9452000 | 8380000 | 8231000 | 7786000 | 7604000 | 7881000 | 8676000 | 8482000 | 8249000 | 10638000 | 11513000 | 11403000 | 11466000 | 8604000 | 7069000 | 7205000 | 6757000 | 7042000 | 7245000 | 6135000 | 8655000 | 10824000 | 9609000 | 11212000 | 9042000 | 6369000 | 8799000 | 5311000 | 4731000 | 6328000 | 6383000 | 7911000 | 9481000 | 5691000 | 9488000 | 7152000 | 8020000 | 6834000 | 6462000 | 6876000 | 7491000 | 8811000 | 6651549 | 7694000 | 7914000 | 10926000 | 8144000 | 10023000 | 6980000 | 8404000 | 8482000 | 8485000 | 7096000 | 7968000 | 8149000 | 7887000 | 8466000 | 10514000 | 14503000 | 9106000 | 10523000 | 10525000 | 7567000 | 7969000 | 7511000 | 6879000 | 7870000 | 7637000 | 10632000 | 11921000 | 10691000 | 12026000 | 11364000 | 7680000 | 9547000 | 6495000 | 6846000 | 6712000 | 6782000 | 8157000 | 8376000 | 11124000 | 10066000 | 9553000 | 10740000 | 10210000 | 7999000 | 7608000 | 6873000 | 7284000 | 6905000 | 6925000 | 7814000 | 7197000 | 9654000 | 10730000 | 10586000 | 9184000 | 6417000 | 7384000 | 7034000 | 6326000 | 6780000 | 7468000 | 8006000 | 7943000 | 12192000 | 10539000 | 12527000 | 8131000 | 7246000 | 7754000 | 7366000 | 7479000 | 6761000 | 6469000 | 9492000 | 7986000 | 8447000 | 11485000 | 8381000 | 8081000 | 7574000 | 6179000 | 7351000 | 5819000 | 6019000 | 5862000 | 7075000 | 9265000 | 9184000 | 11735000 | 11059000 | 9301000 | 10064000 | 8608000 | 7561000 | 8533000 | 6939000 | 7370000 | 9762460 | 7632680 | 12403520 | 10563410 | 9782000 | 7495000 | 6516000 | 7738000 | 6275000 | 5943000 | 6368000 | 5142000 | 6393000 | 9497000 | 8303000 | 10516000 | 9213000 | 8343000 | 6882000 | 6107000 | 9098000 | 7173000 | 5640000 | 5246000 | 6404000 | 9372000 | 9839000 | 11014000 | 10278000 | 7582000 | 7456000 | 8290000
| 8866000 | 10972000 | 13734000 | 10737000 | 11136000 | 9178000 | 9184000 | 7483000 | 7835000 | 7716000 | 7480000 | 7839000 | 8838000 | 9938000 | 7556000 | 10368000 | 9825000 | 7831000 | 8726000 | 7207000 | 8179000 | 7364000 | 7711000 | 8620000 | 9465000 | 9787000 | 10879000 | 11916000 | 11480000 | 8007000 | 7874000 | 7241000 | 8274000 | 7116000 | 6471000 | 6484000 | 9430000 | 10583000 | 10050000 | 11622000 | 7718000 | 7389000 | 6184000 | 6661000 | 5643000 | 6392000 | 5223000 | 4480000 | 5592000 | 8211000 | 5307000 | 7952000 | 8586000 | 6492000 | 7190000 | 6613000 | 5854000 | 7714000 | 6906867 | 7298000 | 8836000 | 10066000 | 9366000 | 8570000 | 9492000 | 9662000 | 8367000 | 6829000 | 6866000 | 8112000 | 7381000 | 8173000 | 7889000 | 12738000 | 12074000 | 10811000 | 11024000 | 9990000 | 8245000 | 6592000 | 6689000 | 7578000 | 7765000 | 7546000 | 12427000 | 10865000 | 10850000 | 12418000 | 11651000 | 7468000 | 8056000 | 7197000 | 7249000 | 7179000 | 6686000 | 7437000 | 9095000 | 9754000 | 11519000 | 9886000 | 9201000 | 9289000 | 8007000 | 8851000 | 6996000 | 6410000 | 7517000 | 6736000 | 7681000 | 8085000 | 10907000 | 11066000 | 8943000 | 10756000 | 7513000 | 7327000 | 6843000 | 7535000 | 6198000 | 6352000 | 8371000 | 7943000 | 12412000 | 11074000 | 11821000 | 7480000 | 7628000 | 6772000 | 7017000 | 7120000 | 7381000 | 6871000 | 9838000 | 7336000 | 9269000 | 10289000 | 8899000 | 7265000 | 6759000 | 7569000 | 7207000 | 6090000 | 6818000 | 6956000 | 6402000 | 9226000 | 9481000 | 12960000 | 11822000 | 8367000 | 8873000 | 7868000 | 8662000 | 7545000 | 8132000 | 7230000 | 7826070 | 8726620 | 9738390 | 11805920 | 8994000 | 7221000 | 4495000 | 8079000 | 6812000 | 6416000 | 6014000 | 5917000 | 7087000 | 9894000 | 9642000 | 9929000 | 9991000 | 7917000 | 6243000 | 5785000 | 8931000 | 6340000 | 6534000 | 4980000 | 7428000 | 9003000 | 9093000 | 9973000 | 11064000 | 8140000 | 6900000 | 7510000
| 7568000 | 10207000 | 11240000 | 12045000 | 10503000 | 7804000 | 9269000 | 8848000 | 7108000 | 7981000 | 7103000 | 7500000 | 9260000 | 10956000 | 7511000 | 10389000 | 10589000 | 8066000 | 9312000 | 7383000 | 7832000 | 7197000 | 6674000 | 7985000 | 8385000 | 9649000 | 10782000 | 10729000 | 9477000 | 8588000 | 7958000 | 6909000 | 7416000 | 7083000 | 7540000 | 6701000 | 9739000 | 9741000 | 10488000 | 9777000 | 7638000 | 7300000 | 7872000 | 5847000 | 6251000 | 6325000 | 6255000 | 4621000 | 5228000 | 12759000 | 5494000 | 9758000 | 9074000 | 6573000 | 6645000 | 6029000 | 7686000 | 8054000 | 8129000 | 6027000 | 8061000 | 7983000 | 8919000 | 10729000 | 7171000 | 8630000 | 8151000 | 7177000 | 7178000 | 7907000 | 8125000 | 8124000 | 7837000 | 10196000 | 9279000 | 9635000 | 10535000 | 7961000 | 7251000 | 7810000 | 6753000 | 7967000 | 8314000 | 7896000 | 9405000 | 10204000 | 11728000 | 11121000 | 9697000 | 7488000 | 6106000 | 7209000 | 6720000 | 6894000 | 7824000 | 7334000 | 9086000 | 9638000 | 9401000 | 12293000 | 9023000 | 9801000 | 6943000 | 8901000 | 6910000 | 6308000 | 7020000 | 8421000 | 7512000 | 7725000 | 10500000 | 9490000 | 10033000 | 10310000 | 7279000 | 6680000 | 7638000 | 7016000 | 6647000 | 6861000 | 8538000 | 7943000 | 11795000 | 12489000 | 10904000 | 7567000 | 7438000 | 6859000 | 6952000 | 7123000 | 6714000 | 7527000 | 9697000 | 7889000 | 11321000 | 11175000 | 9664000 | 7355000 | 7960000 | 6029000 | 6193000 | 7048000 | 6837000 | 6863000 | 6515000 | 9440000 | 8965000 | 12290000 | 10248000 | 9101000 | 9064000 | 7736000 | 7708000 | 7096000 | 7288000 | 7585000 | 7585370 | 10372510 | 8643620 | 11979390 | 7791000 | 7277000 | 7626000 | 7863000 | 6580000 | 6290000 | 6473000 | 6633000 | 6523000 | 8701000 | 10254000 | 10658000 | 8863000 | 8418000 | 6832000 | 6295000 | 8287000 | 5612000 | 5796000 | 5100000 | 6301000 | 9443000 | 10575000 | 9707000 | 9556000 | 7625000 | 7240000 | 7872000
| 7355000 | 10066000 | 10536000 | 13259000 | 9610000 | 7524000 | 8318000 | 6978000 | 7520000 | 7785000 | 8310000 | 7307000 | 9202000 | 9135000 | 7875000 | 9223000 | 10566000 | 8413000 | 8681000 | 7792000 | 7348000 | 8167000 | 7229000 | 8250000 | 9636000 | 9830000 | 12589000 | 10270000 | 8032000 | 8023000 | 8308000 | 7062000 | 7468000 | 6982000 | 6701000 | 6402000 | 8433000 | 9294000 | 8980000 | 10997000 | 7824000 | 6876000 | 7169000 | 6196000 | 6660000 | 6099000 | 7237000 | 5696000 | 7213000 | 7190000 | 8594000 | 10123000 | 8323000 | 7208000 | 6794000 | 7037000 | 7007000 | 7451000 | 6205000 | 7598000 | 8544000 | 10854000 | 10990000 | 9869000 | 8498000 | 8847000 | 7593000 | 6307000 | 7923000 | 8604000 | 8117000 | 7882000 | 7932000 | 9338000 | 7506000 | 10486000 | 11266000 | 7941000 | 7124000 | 7084000 | 7029000 | 7672000 | 8551000 | 7761000 | 9711000 | 11321000 | 11348000 | 11828000 | 11464000 | 7061000 | 6779000 | 7289000 | 7091000 | 6333000 | 7814000 | 7417000 | 7901000 | 11190000 | 11343000 | 11199000 | 10019000 | 8607000 | 7983000 | 6444000 | 7794000 | 7128000 | 6905000 | 7460000 | 8242000 | 9820000 | 11377000 | 10868000 | 10774000 | 9941000 | 7287000 | 7068000 | 9892000 | 7102000 | 6309000 | 7635000 | 8551000 | 8158000 | 11431000 | 11570000 | 10607000 | 7750000 | 7803000 | 6669000 | 6638000 | 8242000 | 6741000 | 7267000 | 9278000 | 8678000 | 10511000 | 10213000 | 8247000 | 7632000 | 6844000 | 6960000 | 7080000 | 6633000 | 5827000 | 6587000 | 6806000 | 10110000 | 9349000 | 10425000 | 9753000 | 9707000 | 8252000 | 8933000 | 7798000 | 7796000 | 7349000 | 7048000 | 7540550 | 10109400 | 7272460 | 11146900 | 8357000 | 7620000 | 7853000 | 7610000 | 6493000 | 6577000 | 5809000 | 7825000 | 7217000 | 8324000 | 8487000 | 10232000 | 9424000 | 8166000 | 6786000 | 6018000 | 7437000 | 7502000 | 6163000 | 5366000 | 5870000 | 9597000 | 8866000 | 9864000 | 10145000 | 7826000 | 7949000
| 9013000 | 11610000 | 10613000 | 11442000 | 10885000 | 8332000 | 8072000 | 7214000 | 10510000 | 7817000 | 7516000 | 10051000 | 8922000 | 9225000 | 8907000 | 9701000 | 9839000 | 8572000 | 8432000 | 6814000 | 7500000 | 7034000 | 8690000 | 8162000 | 8390000 | 8955000 | 12078000 | 9934000 | 8643000 | 8210000 | 7889000 | 7016000 | 6906000 | 6769000 | 6970000 | 6238000 | 7858000 | 9957000 | 9098000 | 10686000 | 7371000 | 6302000 | 7852000 | 5561000 | 6026000 | 7835000 | 5251000 | 8198000 | 6524000 | 5870000 | 10302000 | 9144000 | 7902000 | 6033000 | 6565000 | 6767000 | 6822000 | 8194251 | 6994000 | 7010000 | 7877000 | 7696000 | 11564000 | 8490000 | 7896000 | 9322000 | 7839000 | 7106000 | 6932000 | 8335000 | 7736000 | 7200000 | 7758000 | 9502000 | 7729000 | 11055000 | 11092000 | 8975000 | 6771000 | 7327000 | 6855000 | 7105000 | 8387000 | 7711000 | 9466000 | 12346000 | 11724000 | 10675000 | 11293000 | 7508000 | 8238000 | 6867000 | 7266000 | 6377000 | 6707000 | 7271000 | 7303000 | 9647000 | 12037000 | 11568000 | 11207000 | 8683000 | 7751000 | 6349000 | 7734000 | 6884000 | 6149000 | 6628000 | 7809000 | 7424000 | 9961000 | 9497000 | 8529000 | 9683000 | 7250000 | 7836000 | 7482000 | 8954000 | 6882000 | 7305000 | 8513000 | 10343000 | 9657000 | 10466000 | 11245000 | 7013000 | 6654000 | 6635000 | 6976000 | 7296000 | 7352000 | 6886000 | 8753000 | 8352000 | 10996000 | 11070000 | 8791000 | 7495000 | 5564000 | 5759000 | 6553000 | 6110000 | 6875000 | 6326000 | 6750000 | 9927000 | 10923000 | 12221000 | 9633000 | 9903000 | 7745000 | 9363000 | 7798000 | 7547000 | 6968000 | 7231000 | 7412730 | 9772420 | 7902430 | 9920160 | 8142000 | 6844000 | 7270000 | 7423000 | 6139000 | 7067000 | 5668000 | 7685000 | 6358000 | 9209000 | 8474000 | 11111000 | 9067000 | 6891000 | 6822000 | 4980000 | 6797000 | 6957000 | 6268000 | 7208000 | 6100000 | 6035000 | 9410000 | 10587000 | 9558000 | 7616000 | 7051000
| 9477000 | 11901000 | 9673000 | 10660000 | 10905000 | 8611000 | 7890000 | 7895000 | 10454000 | 7472000 | 7496000 | 6160000 | 8720000 | 8729000 | 9005000 | 10364000 | 10318000 | 8978000 | 8077000 | 7513000 | 8521000 | 7034000 | 7363000 | 7922000 | 7148000 | 9306000 | 13050000 | 10502000 | 9545000 | 7843000 | 7531000 | 7015000 | 6242000 | 6944000 | 6912000 | 7937000 | 8543000 | 10801000 | 9993000 | 10898000 | 7611000 | 6725000 | 7094000 | 6403000 | 6753000 | 4292000 | 3472000 | 4882000 | 5755000 | 5360000 | 11278000 | 8467000 | 7654000 | 5954000 | 6744000 | 7460000 | 6066000 | 6611480 | 6986000 | 6668000 | 8467000 | 7988000 | 11998000 | 12102000 | 8679000 | 6748000 | 7426000 | 7159000 | 8690000 | 7890000 | 7664000 | 8035000 | 6926000 | 10329000 | 11391000 | 10589000 | 9342000 | 10339000 | 7340000 | 6979000 | 7708000 | 8231000 | 9100000 | 9096000 | 9145000 | 11472000 | 11587000 | 12076000 | 9221000 | 8025000 | 8393000 | 7281000 | 6698000 | 7678000 | 7436000 | 7100000 | 7814000 | 8836000 | 10290000 | 8195000 | 7796000 | 8629000 | 7547000 | 7114000 | 6880000 | 7876000 | 8366000 | 7287000 | 8598000 | 7698000 | 10634000 | 9347000 | 9215000 | 9625000 | 7677000 | 7310000 | 7270000 | 6660000 | 6843000 | 6785000 | 8079000 | 8939000 | 9678000 | 10129000 | 11925000 | 9199000 | 8036000 | 7495000 | 6927000 | 7422000 | 7063000 | 6402000 | 7722000 | 8865000 | 9337000 | 11094000 | 8436000 | 9108000 | 7163000 | 6925000 | 7352000 | 6478000 | 7084000 | 6947000 | 7325000 | 9186000 | 11442000 | 12585000 | 12276000 | 10055000 | 8900000 | 7171000 | 8502000 | 7371000 | 6709000 | 6841000 | 7896620 | 9581520 | 8337350 | 7191950 | 8282000 | 7574000 | 7205000 | 7818000 | 7335000 | 6605000 | 6511000 | 6108000 | 7405000 | 9202000 | 9432000 | 11409000 | 9332000 | 6283000 | 6732000 | 5707000 | 7218000 | 7379000 | 6287000 | 5933000 | 6649000 | 6467000 | 8372000 | 10198000 | 8292000 | 7546000 | 7223000
| 9662000 | 10586000 | 8966000 | 11826000 | 11214000 | 9579000 | 8287000 | 7550000 | 9228000 | 8097000 | 8162000 | 8420000 | 7388000 | 9504000 | 8695000 | 9091000 | 9800000 | 8099000 | 8080000 | 7590000 | 7102000 | 7883000 | 7851000 | 7938000 | 8737000 | 9254000 | 14785000 | 11830000 | 10098000 | 8319000 | 7474000 | 6694000 | 6979000 | 7196000 | 7036000 | 7097000 | 7942000 | 11200000 | 11320000 | 8495000 | 7195000 | 6913000 | 6477000 | 6403000 | 5942000 | 4618000 | 4317000 | 4735000 | 9226000 | 5256000 | 9272000 | 8595000 | 6627000 | 6862000 | 6831000 | 5795000 | 7687000 | 8278207 | 6417000 | 6624000 | 7918000 | 5721000 | 11506000 | 9017000 | 8319000 | 8319000 | 7677000 | 7990000 | 9514000 | 7884000 | 7912000 | 7751000 | 8620000 | 10763000 | 14737000 | 10152000 | 9455000 | 10601000 | 7660000 | 6982000 | 7242000 | 8440000 | 8107000 | 7802000 | 11456000 | 12849000 | 11433000 | 11202000 | 11106000 | 8883000 | 7718000 | 7050000 | 6948000 | 7705000 | 7993000 | 7549000 | 9440000 | 8687000 | 9756000 | 11421000 | 8245000 | 8771000 | 7254000 | 7005000 | 7297000 | 6672000 | 6866000 | 7019000 | 7914000 | 8219000 | 8474000 | 9900000 | 9949000 | 7610000 | 6665000 | 6380000 | 7276000 | 6396000 | 7106000 | 7361000 | 7725000 | 6796000 | 10916000 | 12246000 | 11926000 | 7945000 | 7977000 | 6763000 | 7737000 | 7598000 | 7145000 | 7890000 | 8267000 | 9236000 | 8941000 | 10660000 | 8825000 | 9731000 | 7886000 | 6926000 | 5969000 | 6936000 | 6228000 | 6240000 | 6855000 | 9228000 | 10386000 | 13227000 | 10593000 | 9839000 | 8947000 | 6965000 | 7750000 | 6955000 | 7388000 | 7601000 | 7533080 | 10453020 | 9830520 | 9384810 | 8556000 | 6760000 | 7293000 | 6687000 | 6483000 | 5139000 | 5208000 | 6582000 | 7089000 | 9636000 | 9185000 | 10838000 | 8288000 | 7521000 | 6363000 | 5823000 | 7170000 | 9594000 | 5949000 | 5451000 | 7022000 | 7944000 | 8039000 | 10305000 |  | 7138000 | 8522000
| 9918000 | 9481000 | 12859000 | 11356000 | 11873000 | 8936000 | 8459000 | 7376000 | 8103000 | 8065000 | 7537000 | 8177000 | 9336000 | 9980000 | 8026000 | 9928000 | 9594000 | 8446000 | 8066000 | 7052000 | 7809000 | 7998000 | 7474000 | 7934000 | 7188000 | 10110000 | 14903000 | 10426000 | 10088000 | 7379000 | 7411000 | 7541000 | 7146000 | 7572000 | 6804000 | 6605000 | 8865000 | 11598000 | 10664000 | 7637000 | 6572000 | 6436000 | 6381000 | 5701000 | 5396000 | 6749000 | 6529000 | 6047000 | 5924000 | 7740000 | 7780000 | 9671000 | 7530000 | 6684000 |  | 7655000 | 6964000 | 8081034 |  | 7505000 | 9076000 | 8536000 | 10840000 | 9788000 | 7994000 | 7911000 | 8286000 | 6572000 | 8095000 | 8510000 | 8122000 | 7830000 | 8625000 | 12009000 | 11672000 | 12123000 | 10318000 | 9966000 | 7432000 | 6930000 | 7174000 | 6613000 | 8646000 | 8493000 | 12879000 | 13111000 | 11525000 | 11939000 | 14060000 | 7746000 | 7878000 | 7797000 | 7122000 | 6509000 | 6890000 | 7324000 | 9789000 | 9832000 | 8218000 | 11104000 | 9579000 | 9130000 |  | 7169000 | 7497000 | 7599000 | 6751000 | 6906000 | 6910000 | 8128000 | 9018000 | 10286000 | 9780000 | 9384000 | 6921000 | 6856000 | 7547000 | 6537000 | 6958000 | 6821000 | 7405000 | 8339000 | 11206000 | 12434000 | 12099000 | 7197000 |  | 6827000 | 7795000 | 6761000 | 7008000 | 6387000 | 10912000 | 7775000 | 10284000 | 10217000 | 8892000 |  | 7946000 | 6897000 | 6549000 | 5847000 | 7232000 | 6421000 | 7121000 | 8628000 | 11538000 | 12803000 | 11362000 | 10055000 | 9675000 | 6507000 | 8050000 | 6593000 | 7229000 | 7862000 | 7186140 | 12765400 | 11159350 | 10172480 | 9858000 | 7154000 |  | 7629000 | 6146000 | 6094000 | 5690000 | 6519000 | 6006000 | 10210000 | 8843000 | 11321000 | 7960000 | 8793000 |  | 6199000 | 7183000 | 7189000 | 5924000 | 5325000 | 6940000 | 8455000 | 10660000 | 11203000 |  | 7499000 | 8161000
|  | 9668000 | 13267000 | 10553000 | 12130000 |  | 7866000 | 7391000 | 7293000 |  | 7657000 | 7311000 | 9549000 | 8587000 | 8424000 | 10542000 | 11316000 | 8862000 |  | 7361000 | 7664000 | 7613000 | 7208000 | 7307000 | 8408000 | 8903000 | 14083000 | 11426000 | 9740000 | 8039000 |  | 7083000 | 6928000 | 7172000 | 6591000 | 7776000 | 8568000 | 12821000 | 8424000 | 9591000 | 6104000 | 7605000 | 7669000 | 5590000 | 6673000 | 6233000 | 6890000 | 7766000 | 5410000 | 9160000 | 10725000 | 9791000 | 7273000 | 7807000 |  | 5612000 | 6653000 | 8530324 |  | 7028000 | 8970000 | 11093000 | 9578000 | 10294000 | 9772000 |  |  | 8064000 | 8490000 | 7765000 | 7803000 | 7907000 | 8930000 | 10152000 | 11406000 | 11286000 | 9392000 |  | 7697000 | 8644000 | 7069000 | 7241000 | 8031000 | 8926000 |  | 12567000 | 11207000 | 11187000 | 11271000 |  | 7628000 | 7166000 | 8249000 |  | 7517000 | 7719000 | 9548000 | 9059000 | 9423000 | 10112000 | 7778000 | 9239000 |  | 6016000 | 7644000 | 7706000 | 6937000 | 6801000 | 7205000 | 7522000 | 11568000 | 10082000 | 9132000 | 10970000 | 6728000 | 7133000 | 7650000 |  | 6464000 | 7867000 | 8885000 | 7685000 | 11449000 | 12426000 | 11334000 | 8431000 |  | 7199000 | 6947000 | 7223000 | 6872000 | 7337000 | 11007000 | 9907000 | 9850000 | 9169000 | 8866000 |  | 7455000 | 6059000 | 7236000 |  | 6520000 | 6693000 | 6973000 | 11642000 | 10880000 | 13274000 | 11427000 |  | 8840000 | 9711000 | 8045000 | 7786000 | 7796000 | 7539000 |  | 14058540 | 8421180 | 9741710 | 9318000 | 8129000 |  | 8039000 | 6554000 | 6020000 | 6011000 | 6733000 | 6602000 | 9992000 | 9396000 | 11013000 | 6851000 | 7197000 |  | 5577000 | 6205000 | 4950000 | 5610000 | 4897000 | 6250000 | 7893000 | 10669000 | 9848000 |  | 7243000 | 7532000
|  | 11289000 |  | 9521000 | 8784000 |  | 7630000 | 8082000 | 8074000 |  | 8133000 | 8333000 |  | 8914000 | 8749000 |  |  | 8044000 |  | 6550000 | 7988000 |  | 7645000 | 8387000 |  |  | 13495000 |  | 10256000 |  |  | 6807000 | 6615000 |  |  | 6954000 | 9491000 | 10249000 | 7401000 | 8100000 | 6322000 |  |  | 5693000 | 6569000 |  | 5885000 | 4017000 |  | 5346000 | 11289000 |  | 7554000 |  |  | 6950000 | 7557000 | 4954528 |  |  | 7021000 | 8572000 | 8807000 | 9803000 |  |  |  | 5950000 | 9010000 |  |  |  | 8763000 | 12082000 | 11727000 | 10843000 |  |  | 6733000 | 7253000 | 7450000 | 7377000 |  | 9112000 |  | 14482000 | 10357000 | 11562000 | 8835000 |  | 6838000 | 7217000 | 7955000 |  | 7505000 | 8269000 |  | 9975000 | 11320000 |  | 9713000 |  |  | 6905000 | 7376000 |  |  | 6781000 | 8115000 | 7131000 | 8877000 |  | 8410000 |  |  | 5952000 | 9456000 |  | 6600000 |  |  | 8314000 |  |  | 10154000 | 10591000 |  | 7209000 | 6379000 |  | 7974000 |  | 8721000 | 10479000 | 10640000 | 9892000 | 9520000 |  |  | 7598000 | 6717000 |  |  | 6646000 | 6427000 |  | 10846000 |  |  |  | 8989000 | 10845000 | 7378000 |  |  | 7348000 |  | 12878280 | 9299320 | 10723600 | 8336000 | 6927000 |  | 7657000 | 6534000 |  | 5180000 | 6622000 |  | 8222000 | 9783000 | 11012000 | 7025000 | 7966000 |  | 5863000 | 5662000 |  | 4809000 | 5664000 |  | 8042000 | 10533000 | 9423000
|  | 13280000 |  |  | 8693000 |  |  | 7062000 | 7990000 |  |  | 6692000 |  |  | 9091000 |  |  | 7656000 |  | 7401000 | 7661000 |  |  | 8293000 |  |  | 11204000 |  | 9680000 |  |  | 6921000 | 6961000 |  |  | 6706000 |  |  | 9556000 |  | 6336000 |  |  | 5495000 |  |  | 4507000 |  |  | 5359000 |  |  | 6673000 |  |  | 7874000 | 6160000 | 6710130 |  |  | 7757000 |  |  | 6973000 |  |  |  | 7594000 | 7809000 |  |  |  | 8757000 |  | 12878000 |  |  |  | 7449000 | 6402000 | 7742000 |  |  | 8908000 |  |  | 11129000 |  |  |  | 7098000 | 7556000 | 8054000 |  |  | 7186000 |  | 10145000 |  |  | 10562000 |  |  | 6721000 |  |  |  | 6935000 |  | 8645000 |  |  | 9662000 |  |  | 6577000 | 8691000 |  | 6554000 |  |  | 9831000 |  |  | 10220000 | 8566000 |  | 6669000 | 6388000 |  | 6410000 |  | 9470000 | 10274000 |  | 10449000 |  |  |  | 6959000 | 6556000 |  |  | 6194000 | 6777000 |  | 11963000 |  |  |  |  | 7084000 | 7918000 |  |  | 7479000 |  |  | 7975470 |  |  | 7314000 |  | 7329000 | 6630000 |  |  | 6757000 |  |  | 11148000 |  |  | 6209000 |  | 5712000 | 6234000 |  |  | 5574000 |  |  | 10106000 | 11060000
|  | 14715000 |  |  | 8736000 |  |  | 7720000 | 7411000 |  |  | 7651000 |  |  | 7615000 |  |  | 7882000 |  |  | 8305000 |  |  | 7956000 |  |  | 9514000 |  | 9616000 |  |  |  | 7088000 |  |  | 7284000 |  |  | 10355000 |  | 6967000 |  |  | 5984000 |  |  | 5833000 |  |  | 5231000 |  |  | 8060000 |  |  | 4113000 |  | 6338189 |  |  | 8406000 |  |  | 8261000 |  |  |  | 6666000 | 8509000 |  |  |  | 8952000 |  | 10511000 |  |  |  | 7638000 |  | 7138000 |  |  | 8409000 |  |  | 12309000 | [5 empty] | 6707000 |  |  | 6569000 |  | 8270000 |  |  | 9534000 |  |  | 7830000 | [5 empty] | 9250000 |  |  | 8936000 |  |  | 7480000 |  |  | 7571000 |  |  | 10318000 |  |  | 9072000 |  |  | 6990000 | [5 empty] | 8250000 |  | 10155000 |  |  |  | 6611000 | 6738000 | [5 empty] | 11360000 |  |  |  |  | 6491000 | 8851000 |  |  | 7155000 |  |  | 8824560 |  |  | 7465000 |  |  | 6753000 |  |  | 6523000 |  |  | 8918000 |  |  | 6287000 |  |  | 5712000 |  |  | 6285000 |  |  | 10014000 | 11051000
[5 empty] | 9289000 |  |  | 7527000 | 6938000 | [5 empty] | 9596000 | [5 empty] | 7770000 | [5 empty] | 11674000 | [16 empty] | 5998000 | [5 empty] | 9244000 |  |  | 7105000 |  |  | 7016000 |  | 6456009 |  |  | 7889000 |  |  | 8191000 |  |  |  | 7667000 | 8279000 |  |  |  | 9783000 | [7 empty] | 7364000 | [11 empty] | 6484000 |  |  | 6576000 |  |  |  |  | 9418000 |  |  | 7605000 | [5 empty] | 9766000 |  |  | 9916000 | [8 empty] | 10111000 | [5 empty] | 6905000 | [7 empty] | 10067000 |  |  |  | 7205000 | 7039000 | [5 empty] | 9830000 |  |  |  |  | 7622000 | 8214000 |  |  | 7549000 | [17 empty] | 7302000 | [9 empty] | 9995000
[9 empty] | 7360000 | [17 empty] | 11096000 | [28 empty] | 6023000 | [11 empty] | 7667000 | [27 empty] | 8591000 | [7 empty] | 7872000 | [17 empty] | 9016000 | [18 empty] | 7393000 | [5 empty] | 10497000 |  |  |  |  | 8408000 | [31 empty] | 9928000
10308000
8849000
Total | 247607000 | 321529000 | 331922000 | 361969000 | 331062000 | 247281000 | 255460000 | 259840000 | 262171000 | 224293000 | 230473000 | 247443000 | 248042000 | 283327000 | 282383000 | 270330000 | 308102000 | 282544000 | 228391000 | 233977000 | 253609000 | 227457000 | 227262000 | 248427000 | 236883000 | 281376000 | 366238000 | 313284000 | 324753000 | 248938000 | 220017000 | 224094000 | 228356000 | 206245000 | 206159000 | 219820000 | 238993000 | 285071000 | 288935000 | 315916000 | 258474000 | 204522000 | 195351000 | 210619000 | 186524000 | 180062000 | 186061000 | 177826000 | 189223000 | 237157000 | 254546000 | 259996000 | 267501000 | 202945000 | 197951000 | 230380000 | 202002000 | 241435152 | 185486773 | 197870000 | 248282000 | 267332000 | 277465000 | 322472000 | 263947000 | 239201000 | 226318000 | 254520000 | 254128000 | 232694000 | 231142000 | 227781000 | 260865000 | 295402000 | 350635000 | 309479000 | 292271000 | 284516000 | 258210000 | 224985000 | 235884000 | 220638000 | 231213000 | 258336000 | 253868000 | 378508000 | 360966000 | 344742000 | 327372000 | 249766000 | 247848000 | 224763000 | 231949000 | 195160000 | 220975000 | 248486000 | 246072000 | 313686000 | 323872000 | 331143000 | 336311000 | 278762000 | 228097000 | 253867000 | 222149000 | 213822000 | 206473000 | 217654000 | 228703000 | 276579000 | 292399000 | 282322000 | 332893000 | 279408000 | 235099000 | 223517000 | 228264000 | 212838000 | 217569000 | 200284000 | 220054000 | 281050000 | 311397000 | 305921000 | 345305000 | 270273000 | 218219000 | 235964000 | 217412000 | 211578000 | 221910000 | 204801000 | 253883000 | 276728000 | 273559000 | 339399000 | 284114000 | 225723000 | 213588000 | 225100000 | 233088000 | 184510000 | 190777000 | 218376000 | 210451000 | 250742000 | 369508000 | 341545000 | 327843000 | 282509000 | 280992000 | 287664000 | 264158000 | 223908000 | 211016000 | 239664000 | 211782020 | 298285400 | 314913620 | 304917930 | 274017890 | 245412000 | 192398000 | 234733000 | 220351000 | 189653000 | 178922000 | 212364000 | 194563000 | 260371000 | 296255000 | 315194000 | 276237000 | 258160000 | 178387000 | 187628000 | 204862000 | 195635000 | 182536000 | 183616000 | 188152000 | 238739000 | 305062000 | 361332000 | 234375000 | 229357000 | 212299000
Avg daily | 8843107.1429 | 10047781.25 | 11445586.2069 | 12065633.3333 | 10032181.8182 | 8831464.2857 | 8515333.3333 | 7873939.3939 | 7710911.7647 | 8010464.2857 | 7682433.3333 | 7732593.75 | 8553172.4138 | 9444233.3333 | 8557060.6061 | 9321724.1379 | 10624206.8966 | 8829500 | 8156821.4286 | 7547645.1613 | 7685121.2121 | 7846535.7143 | 7575400 | 7763343.75 | 8168379.3103 | 9702620.6897 | 10771705.8824 | 10802896.5517 | 10148531.25 | 8584068.9655 | 7859407.4074 | 7228838.7097 | 7136125 | 7111896.5517 | 7108931.0345 | 6869375 | 7966433.3333 | 9502366.6667 | 9029218.75 | 10530533.3333 | 8077312.5 | 7052482.7586 | 6736241.3793 | 6382393.9394 | 6217466.6667 | 6209034.4828 | 5814406.25 | 5927533.3333 | 6524931.0345 | 7186575.7576 | 8484866.6667 | 8965379.3103 | 8106090.9091 | 6998103.4483 | 7331518.5185 | 6775882.3529 | 6516193.5484 | 7316216.7273 | 6869880.4815 | 6823103.4483 | 7523696.9697 | 8911066.6667 | 9248833.3333 | 9771878.7879 | 9101620.6897 | 8542892.8571 | 8082785.7143 | 7485882.3529 | 7700848.4848 | 8023931.0345 | 7970413.7931 | 7854517.2414 | 7905000 | 9846733.3333 | 10957343.75 | 10315966.6667 | 10078310.3448 | 10161285.7143 | 8069062.5 | 7257580.6452 | 7148000 | 7354600 | 7972862.069 | 8073000 | 9066714.2857 | 12616933.3333 | 11280187.5 | 11491400 | 10912400 | 8920214.2857 | 7995096.7742 | 7250419.3548 | 7028757.5758 | 6970000 | 7365833.3333 | 7308411.7647 | 8485241.3793 | 9802687.5 | 10795733.3333 | 11418724.1379 | 10191242.4242 | 9612482.7586 | 8448037.037 | 7466676.4706 | 7404966.6667 | 7373172.4138 | 7119758.6207 | 7021096.7742 | 7623433.3333 | 8381181.8182 | 9746633.3333 | 9735241.3793 | 10087666.6667 | 9634758.6207 | 8106862.069 | 6984906.25 | 7363354.8387 | 7601357.1429 | 6799031.25 | 6906344.8276 | 7588068.9655 | 8266176.4706 | 10737827.5862 | 10549000 | 10790781.25 | 8718483.871 | 8082185.1852 | 7150424.2424 | 7013290.3226 | 7295793.1034 | 7158387.0968 | 7062103.4483 | 8189774.1935 | 8647750 | 9118633.3333 | 10284818.1818 | 9470466.6667 | 8360111.1111 | 7365103.4483 | 6821212.1212 | 6855529.4118 | 6589642.8571 | 6578517.2414 | 7044387.0968 | 6788741.9355 | 8646275.8621 | 10867882.3529 | 11777413.7931 | 11304931.0345 | 10089607.1429 | 9366400 | 8460705.8824 | 8004787.8788 | 7720965.5172 | 7276413.7931 | 7262545.4545 | 7563643.5714 | 9942846.6667 | 9841050.625 | 10163931 | 9133929.6667 | 7669125 | 7125851.8519 | 7572032.2581 | 6885968.75 | 6539758.6207 | 5964066.6667 | 6636375 | 6709068.9655 | 8679033.3333 | 9257968.75 | 10506466.6667 | 9207900 | 7823030.303 | 6606925.9259 | 6052516.129 | 6401937.5 | 6746034.4828 | 6084533.3333 | 5738000 | 6488000 | 7957966.6667 | 9517677.4194 | 10037000 | 9014423.0769 | 7908862.069 | 7320655.1724